## Revisions & Definitions
Revision history
| Release date | CU Firmware version | Changes
| 2016-12-06 | v.1.09 or earlier
| 2019-01-10 | v.2.00 or later | Input Registers: PI Regulation Output - Value and range changed from 0-255 HEX to percentage 0-100%
Note! With RU software version v2.00, room units will round the setpoint to nearest value multiple of 0.5°C when changing setpoint from room unit user interface.
Example: If the setpoint is set to 22.3°C and user increases the setpoint, then it is changed to 22.5 instead of 22.8. If setpoint is not changed then the odd setpoint is still used.
Definitions
| CU | Central Unit | General term for Receiver. Two models exists: 8 and 1 channel / zones
| CU8 | 8 channel Central Unit | A CU8 can act as stand-alone master, a slave in a network or as master which hosts a radio based network of CU's and if required RUR's. It also supports Modbus RTU with access to the whole network.
| CU1 | 1 channel Central Unit | A CU8 can act as stand-alone master or as slave in a network (not network master). It supports a radio based communication in a network of CU's and if required RUR's.
| RU | Room Unit | General term for room unit = Thermostat
| RUW | Wired RU | Cabled RU powered by the bus cable
| RUR | Radio based RU | Wireless RU which is battery operated
| Zone | Area controlled by one RU | 8 zones per CU. Up to 64 zones available in a network consisting of 8 CU's. Zone numbers will be assinged in order of pairing within each CU.
| Master | Main CU in network | If only one CU is used, this will still be set as Master. The master is always CU1
| Slave | Secondary CU in network | A slave will be assinged number CU2 … CU8 in order of pairing

## Coils
Modbus | Range | Register | Min | Max | Unit | Notes
0:00001 | System | Production test mode | 0 | 1
0:01001 | Zone 1 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01002 | Zone 1 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01003 | Zone 1 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01004 | Zone 1 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01101 | Zone 2 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01102 | Zone 2 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01103 | Zone 2 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01104 | Zone 2 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01201 | Zone 3 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01202 | Zone 3 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01203 | Zone 3 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01204 | Zone 3 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01301 | Zone 4 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01302 | Zone 4 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01303 | Zone 4 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01304 | Zone 4 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01401 | Zone 5 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01402 | Zone 5 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01403 | Zone 5 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01404 | Zone 5 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01501 | Zone 6 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01502 | Zone 6 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01503 | Zone 6 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01504 | Zone 6 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01601 | Zone 7 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01602 | Zone 7 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01603 | Zone 7 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01604 | Zone 7 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01701 | Zone 8 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01702 | Zone 8 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01703 | Zone 8 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01704 | Zone 8 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01801 | Zone 9 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01802 | Zone 9 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01803 | Zone 9 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01804 | Zone 9 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:01901 | Zone 10 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:01902 | Zone 10 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:01903 | Zone 10 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:01904 | Zone 10 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02001 | Zone 11 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02002 | Zone 11 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02003 | Zone 11 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02004 | Zone 11 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02101 | Zone 12 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02102 | Zone 12 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02103 | Zone 12 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02104 | Zone 12 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02201 | Zone 13 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02202 | Zone 13 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02203 | Zone 13 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02204 | Zone 13 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02301 | Zone 14 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02302 | Zone 14 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02303 | Zone 14 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02304 | Zone 14 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02401 | Zone 15 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02402 | Zone 15 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02403 | Zone 15 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02404 | Zone 15 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02501 | Zone 16 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02502 | Zone 16 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02503 | Zone 16 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02504 | Zone 16 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02601 | Zone 17 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02602 | Zone 17 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02603 | Zone 17 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02604 | Zone 17 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02701 | Zone 18 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02702 | Zone 18 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02703 | Zone 18 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02704 | Zone 18 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02801 | Zone 19 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02802 | Zone 19 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02803 | Zone 19 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02804 | Zone 19 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:02901 | Zone 20 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:02902 | Zone 20 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:02903 | Zone 20 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:02904 | Zone 20 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03001 | Zone 21 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03002 | Zone 21 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03003 | Zone 21 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03004 | Zone 21 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03101 | Zone 22 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03102 | Zone 22 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03103 | Zone 22 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03104 | Zone 22 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03201 | Zone 23 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03202 | Zone 23 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03203 | Zone 23 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03204 | Zone 23 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03301 | Zone 24 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03302 | Zone 24 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03303 | Zone 24 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03304 | Zone 24 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03401 | Zone 25 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03402 | Zone 25 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03403 | Zone 25 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03404 | Zone 25 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03501 | Zone 26 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03502 | Zone 26 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03503 | Zone 26 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03504 | Zone 26 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03601 | Zone 27 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03602 | Zone 27 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03603 | Zone 27 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03604 | Zone 27 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03701 | Zone 28 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03702 | Zone 28 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03703 | Zone 28 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03704 | Zone 28 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03801 | Zone 29 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03802 | Zone 29 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03803 | Zone 29 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03804 | Zone 29 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:03901 | Zone 30 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:03902 | Zone 30 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:03903 | Zone 30 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:03904 | Zone 30 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04001 | Zone 31 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04002 | Zone 31 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04003 | Zone 31 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04004 | Zone 31 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04101 | Zone 32 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04102 | Zone 32 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04103 | Zone 32 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04104 | Zone 32 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04201 | Zone 33 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04202 | Zone 33 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04203 | Zone 33 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04204 | Zone 33 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04301 | Zone 34 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04302 | Zone 34 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04303 | Zone 34 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04304 | Zone 34 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04401 | Zone 35 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04402 | Zone 35 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04403 | Zone 35 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04404 | Zone 35 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04501 | Zone 36 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04502 | Zone 36 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04503 | Zone 36 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04504 | Zone 36 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04601 | Zone 37 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04602 | Zone 37 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04603 | Zone 37 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04604 | Zone 37 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04701 | Zone 38 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04702 | Zone 38 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04703 | Zone 38 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04704 | Zone 38 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04801 | Zone 39 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04802 | Zone 39 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04803 | Zone 39 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04804 | Zone 39 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:04901 | Zone 40 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:04902 | Zone 40 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:04903 | Zone 40 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:04904 | Zone 40 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05001 | Zone 41 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05002 | Zone 41 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05003 | Zone 41 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05004 | Zone 41 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05101 | Zone 42 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05102 | Zone 42 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05103 | Zone 42 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05104 | Zone 42 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05201 | Zone 43 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05202 | Zone 43 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05203 | Zone 43 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05204 | Zone 43 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05301 | Zone 44 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05302 | Zone 44 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05303 | Zone 44 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05304 | Zone 44 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05401 | Zone 45 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05402 | Zone 45 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05403 | Zone 45 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05404 | Zone 45 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05501 | Zone 46 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05502 | Zone 46 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05503 | Zone 46 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05504 | Zone 46 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05601 | Zone 47 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05602 | Zone 47 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05603 | Zone 47 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05604 | Zone 47 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05701 | Zone 48 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05702 | Zone 48 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05703 | Zone 48 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05704 | Zone 48 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05801 | Zone 49 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05802 | Zone 49 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05803 | Zone 49 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05804 | Zone 49 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:05901 | Zone 50 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:05902 | Zone 50 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:05903 | Zone 50 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:05904 | Zone 50 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06001 | Zone 51 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06002 | Zone 51 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06003 | Zone 51 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06004 | Zone 51 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06101 | Zone 52 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06102 | Zone 52 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06103 | Zone 52 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06104 | Zone 52 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06201 | Zone 53 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06202 | Zone 53 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06203 | Zone 53 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06204 | Zone 53 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06301 | Zone 54 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06302 | Zone 54 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06303 | Zone 54 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06304 | Zone 54 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06401 | Zone 55 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06402 | Zone 55 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06403 | Zone 55 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06404 | Zone 55 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06501 | Zone 56 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06502 | Zone 56 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06503 | Zone 56 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06504 | Zone 56 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06601 | Zone 57 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06602 | Zone 57 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06603 | Zone 57 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06604 | Zone 57 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06701 | Zone 58 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06702 | Zone 58 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06703 | Zone 58 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06704 | Zone 58 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06801 | Zone 59 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06802 | Zone 59 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06803 | Zone 59 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06804 | Zone 59 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:06901 | Zone 60 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:06902 | Zone 60 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:06903 | Zone 60 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:06904 | Zone 60 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:07001 | Zone 61 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:07002 | Zone 61 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:07003 | Zone 61 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:07004 | Zone 61 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:07101 | Zone 62 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:07102 | Zone 62 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:07103 | Zone 62 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:07104 | Zone 62 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:07201 | Zone 63 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:07202 | Zone 63 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:07203 | Zone 63 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:07204 | Zone 63 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:07301 | Zone 64 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:07302 | Zone 64 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:07303 | Zone 64 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:07304 | Zone 64 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11001 | Zone 1 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11002 | Zone 2 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11003 | Zone 3 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11004 | Zone 4 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11005 | Zone 5 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11006 | Zone 6 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11007 | Zone 7 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11008 | Zone 8 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11009 | Zone 9 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11010 | Zone 10 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11011 | Zone 11 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11012 | Zone 12 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11013 | Zone 13 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11014 | Zone 14 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11015 | Zone 15 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11016 | Zone 16 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11017 | Zone 17 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11018 | Zone 18 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11019 | Zone 19 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11020 | Zone 20 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11021 | Zone 21 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11022 | Zone 22 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11023 | Zone 23 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11024 | Zone 24 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11025 | Zone 25 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11026 | Zone 26 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11027 | Zone 27 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11028 | Zone 28 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11029 | Zone 29 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11030 | Zone 30 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11031 | Zone 31 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11032 | Zone 32 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11033 | Zone 33 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11034 | Zone 34 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11035 | Zone 35 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11036 | Zone 36 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11037 | Zone 37 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11038 | Zone 38 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11039 | Zone 39 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11040 | Zone 40 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11041 | Zone 41 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11042 | Zone 42 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11043 | Zone 43 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11044 | Zone 44 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11045 | Zone 45 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11046 | Zone 46 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11047 | Zone 47 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11048 | Zone 48 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11049 | Zone 49 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11050 | Zone 50 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11051 | Zone 51 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11052 | Zone 52 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11053 | Zone 53 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11054 | Zone 54 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11055 | Zone 55 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11056 | Zone 56 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11057 | Zone 57 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11058 | Zone 58 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11059 | Zone 59 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11060 | Zone 60 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11061 | Zone 61 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11062 | Zone 62 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11063 | Zone 63 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11064 | Zone 64 | Week Program Enable | 0 | 1 |  | 0 - Week Program Disabled, 1 - Week Program Enabled.
0:11065 | Zone 1 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11066 | Zone 2 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11067 | Zone 3 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11068 | Zone 4 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11069 | Zone 5 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11070 | Zone 6 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11071 | Zone 7 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11072 | Zone 8 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11073 | Zone 9 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11074 | Zone 10 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11075 | Zone 11 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11076 | Zone 12 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11077 | Zone 13 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11078 | Zone 14 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11079 | Zone 15 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11080 | Zone 16 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11081 | Zone 17 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11082 | Zone 18 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11083 | Zone 19 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11084 | Zone 20 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11085 | Zone 21 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11086 | Zone 22 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11087 | Zone 23 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11088 | Zone 24 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11089 | Zone 25 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11090 | Zone 26 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11091 | Zone 27 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11092 | Zone 28 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11093 | Zone 29 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11094 | Zone 30 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11095 | Zone 31 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11096 | Zone 32 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11097 | Zone 33 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11098 | Zone 34 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11099 | Zone 35 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11100 | Zone 36 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11101 | Zone 37 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11102 | Zone 38 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11103 | Zone 39 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11104 | Zone 40 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11105 | Zone 41 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11106 | Zone 42 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11107 | Zone 43 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11108 | Zone 44 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11109 | Zone 45 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11110 | Zone 46 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11111 | Zone 47 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11112 | Zone 48 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11113 | Zone 49 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11114 | Zone 50 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11115 | Zone 51 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11116 | Zone 52 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11117 | Zone 53 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11118 | Zone 54 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11119 | Zone 55 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11120 | Zone 56 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11121 | Zone 57 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11122 | Zone 58 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11123 | Zone 59 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11124 | Zone 60 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11125 | Zone 61 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11126 | Zone 62 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11127 | Zone 63 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11128 | Zone 64 | Adaptive Control Enable | 0 | 1 |  | 0 - Adaptive Control Disabled, 1 - Adaptive Control Enabled.
0:11129 | Zone 1 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11130 | Zone 2 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11131 | Zone 3 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11132 | Zone 4 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11133 | Zone 5 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11134 | Zone 6 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11135 | Zone 7 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11136 | Zone 8 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11137 | Zone 9 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11138 | Zone 10 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11139 | Zone 11 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11140 | Zone 12 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11141 | Zone 13 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11142 | Zone 14 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11143 | Zone 15 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11144 | Zone 16 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11145 | Zone 17 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11146 | Zone 18 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11147 | Zone 19 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11148 | Zone 20 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11149 | Zone 21 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11150 | Zone 22 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11151 | Zone 23 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11152 | Zone 24 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11153 | Zone 25 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11154 | Zone 26 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11155 | Zone 27 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11156 | Zone 28 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11157 | Zone 29 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11158 | Zone 30 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11159 | Zone 31 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11160 | Zone 32 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11161 | Zone 33 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11162 | Zone 34 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11163 | Zone 35 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11164 | Zone 36 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11165 | Zone 37 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11166 | Zone 38 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11167 | Zone 39 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11168 | Zone 40 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11169 | Zone 41 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11170 | Zone 42 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11171 | Zone 43 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11172 | Zone 44 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11173 | Zone 45 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11174 | Zone 46 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11175 | Zone 47 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11176 | Zone 48 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11177 | Zone 49 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11178 | Zone 50 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11179 | Zone 51 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11180 | Zone 52 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11181 | Zone 53 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11182 | Zone 54 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11183 | Zone 55 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11184 | Zone 56 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11185 | Zone 57 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11186 | Zone 58 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11187 | Zone 59 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11188 | Zone 60 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11189 | Zone 61 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11190 | Zone 62 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11191 | Zone 63 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11192 | Zone 64 | Backlight Enable | 0 | 1 |  | 0 - Backlight Disabled, 1 - Backlight Enabled.
0:11193 | Zone 1 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11194 | Zone 2 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11195 | Zone 3 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11196 | Zone 4 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11197 | Zone 5 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11198 | Zone 6 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11199 | Zone 7 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11200 | Zone 8 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11201 | Zone 9 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11202 | Zone 10 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11203 | Zone 11 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11204 | Zone 12 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11205 | Zone 13 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11206 | Zone 14 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11207 | Zone 15 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11208 | Zone 16 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11209 | Zone 17 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11210 | Zone 18 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11211 | Zone 19 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11212 | Zone 20 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11213 | Zone 21 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11214 | Zone 22 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11215 | Zone 23 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11216 | Zone 24 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11217 | Zone 25 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11218 | Zone 26 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11219 | Zone 27 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11220 | Zone 28 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11221 | Zone 29 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11222 | Zone 30 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11223 | Zone 31 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11224 | Zone 32 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11225 | Zone 33 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11226 | Zone 34 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11227 | Zone 35 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11228 | Zone 36 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11229 | Zone 37 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11230 | Zone 38 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11231 | Zone 39 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11232 | Zone 40 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11233 | Zone 41 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11234 | Zone 42 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11235 | Zone 43 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11236 | Zone 44 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11237 | Zone 45 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11238 | Zone 46 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11239 | Zone 47 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11240 | Zone 48 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11241 | Zone 49 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11242 | Zone 50 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11243 | Zone 51 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11244 | Zone 52 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11245 | Zone 53 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11246 | Zone 54 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11247 | Zone 55 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11248 | Zone 56 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11249 | Zone 57 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11250 | Zone 58 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11251 | Zone 59 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11252 | Zone 60 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11253 | Zone 61 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11254 | Zone 62 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11255 | Zone 63 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.
0:11256 | Zone 64 | Keylock Enable | 0 | 1 |  | 0 - Keylock Disabled, 1 - Keylock Enabled.

## Inputs
Modbus | Range | Register | Min | Max | Unit | Notes
1:00001 | System | Global Pump State | 0 | 1 |  | 0 - Pump Not Active, 1 - Pump Active.
1:00002 | System | Global Boiler State | 0 | 1 |  | 0 - Boiler Not Active, 1 - Boiler Active.
1:00003 | System | Global Bypass Hold State | 0 | 1
1:00004 | System | Global Bypass State | 0 | 1 |  | 0 - Bypass not available in system, 1 - Bypass available in system
1:01001 | Zone 1 | Zone is defined in CU | 0 | 1
1:01002 | Zone 1 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01003 | Zone 1 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01004 | Zone 1 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01005 | Zone 1 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01101 | Zone 2 | Zone is defined in CU | 0 | 1
1:01102 | Zone 2 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01103 | Zone 2 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01104 | Zone 2 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01105 | Zone 2 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01201 | Zone 3 | Zone is defined in CU | 0 | 1
1:01202 | Zone 3 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01203 | Zone 3 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01204 | Zone 3 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01205 | Zone 3 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01301 | Zone 4 | Zone is defined in CU | 0 | 1
1:01302 | Zone 4 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01303 | Zone 4 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01304 | Zone 4 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01305 | Zone 4 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01401 | Zone 5 | Zone is defined in CU | 0 | 1
1:01402 | Zone 5 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01403 | Zone 5 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01404 | Zone 5 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01405 | Zone 5 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01501 | Zone 6 | Zone is defined in CU | 0 | 1
1:01502 | Zone 6 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01503 | Zone 6 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01504 | Zone 6 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01505 | Zone 6 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01601 | Zone 7 | Zone is defined in CU | 0 | 1
1:01602 | Zone 7 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01603 | Zone 7 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01604 | Zone 7 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01605 | Zone 7 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01701 | Zone 8 | Zone is defined in CU | 0 | 1
1:01702 | Zone 8 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01703 | Zone 8 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01704 | Zone 8 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01705 | Zone 8 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01801 | Zone 9 | Zone is defined in CU | 0 | 1
1:01802 | Zone 9 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01803 | Zone 9 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01804 | Zone 9 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01805 | Zone 9 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:01901 | Zone 10 | Zone is defined in CU | 0 | 1
1:01902 | Zone 10 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:01903 | Zone 10 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:01904 | Zone 10 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:01905 | Zone 10 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02001 | Zone 11 | Zone is defined in CU | 0 | 1
1:02002 | Zone 11 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02003 | Zone 11 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02004 | Zone 11 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02005 | Zone 11 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02101 | Zone 12 | Zone is defined in CU | 0 | 1
1:02102 | Zone 12 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02103 | Zone 12 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02104 | Zone 12 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02105 | Zone 12 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02201 | Zone 13 | Zone is defined in CU | 0 | 1
1:02202 | Zone 13 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02203 | Zone 13 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02204 | Zone 13 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02205 | Zone 13 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02301 | Zone 14 | Zone is defined in CU | 0 | 1
1:02302 | Zone 14 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02303 | Zone 14 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02304 | Zone 14 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02305 | Zone 14 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02401 | Zone 15 | Zone is defined in CU | 0 | 1
1:02402 | Zone 15 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02403 | Zone 15 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02404 | Zone 15 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02405 | Zone 15 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02501 | Zone 16 | Zone is defined in CU | 0 | 1
1:02502 | Zone 16 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02503 | Zone 16 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02504 | Zone 16 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02505 | Zone 16 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02601 | Zone 17 | Zone is defined in CU | 0 | 1
1:02602 | Zone 17 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02603 | Zone 17 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02604 | Zone 17 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02605 | Zone 17 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02701 | Zone 18 | Zone is defined in CU | 0 | 1
1:02702 | Zone 18 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02703 | Zone 18 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02704 | Zone 18 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02705 | Zone 18 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02801 | Zone 19 | Zone is defined in CU | 0 | 1
1:02802 | Zone 19 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02803 | Zone 19 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02804 | Zone 19 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02805 | Zone 19 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:02901 | Zone 20 | Zone is defined in CU | 0 | 1
1:02902 | Zone 20 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:02903 | Zone 20 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:02904 | Zone 20 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:02905 | Zone 20 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03001 | Zone 21 | Zone is defined in CU | 0 | 1
1:03002 | Zone 21 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03003 | Zone 21 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03004 | Zone 21 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03005 | Zone 21 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03101 | Zone 22 | Zone is defined in CU | 0 | 1
1:03102 | Zone 22 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03103 | Zone 22 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03104 | Zone 22 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03105 | Zone 22 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03201 | Zone 23 | Zone is defined in CU | 0 | 1
1:03202 | Zone 23 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03203 | Zone 23 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03204 | Zone 23 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03205 | Zone 23 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03301 | Zone 24 | Zone is defined in CU | 0 | 1
1:03302 | Zone 24 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03303 | Zone 24 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03304 | Zone 24 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03305 | Zone 24 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03401 | Zone 25 | Zone is defined in CU | 0 | 1
1:03402 | Zone 25 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03403 | Zone 25 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03404 | Zone 25 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03405 | Zone 25 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03501 | Zone 26 | Zone is defined in CU | 0 | 1
1:03502 | Zone 26 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03503 | Zone 26 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03504 | Zone 26 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03505 | Zone 26 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03601 | Zone 27 | Zone is defined in CU | 0 | 1
1:03602 | Zone 27 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03603 | Zone 27 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03604 | Zone 27 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03605 | Zone 27 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03701 | Zone 28 | Zone is defined in CU | 0 | 1
1:03702 | Zone 28 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03703 | Zone 28 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03704 | Zone 28 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03705 | Zone 28 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03801 | Zone 29 | Zone is defined in CU | 0 | 1
1:03802 | Zone 29 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03803 | Zone 29 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03804 | Zone 29 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03805 | Zone 29 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:03901 | Zone 30 | Zone is defined in CU | 0 | 1
1:03902 | Zone 30 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:03903 | Zone 30 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:03904 | Zone 30 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:03905 | Zone 30 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04001 | Zone 31 | Zone is defined in CU | 0 | 1
1:04002 | Zone 31 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04003 | Zone 31 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04004 | Zone 31 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04005 | Zone 31 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04101 | Zone 32 | Zone is defined in CU | 0 | 1
1:04102 | Zone 32 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04103 | Zone 32 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04104 | Zone 32 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04105 | Zone 32 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04201 | Zone 33 | Zone is defined in CU | 0 | 1
1:04202 | Zone 33 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04203 | Zone 33 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04204 | Zone 33 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04205 | Zone 33 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04301 | Zone 34 | Zone is defined in CU | 0 | 1
1:04302 | Zone 34 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04303 | Zone 34 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04304 | Zone 34 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04305 | Zone 34 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04401 | Zone 35 | Zone is defined in CU | 0 | 1
1:04402 | Zone 35 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04403 | Zone 35 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04404 | Zone 35 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04405 | Zone 35 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04501 | Zone 36 | Zone is defined in CU | 0 | 1
1:04502 | Zone 36 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04503 | Zone 36 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04504 | Zone 36 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04505 | Zone 36 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04601 | Zone 37 | Zone is defined in CU | 0 | 1
1:04602 | Zone 37 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04603 | Zone 37 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04604 | Zone 37 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04605 | Zone 37 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04701 | Zone 38 | Zone is defined in CU | 0 | 1
1:04702 | Zone 38 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04703 | Zone 38 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04704 | Zone 38 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04705 | Zone 38 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04801 | Zone 39 | Zone is defined in CU | 0 | 1
1:04802 | Zone 39 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04803 | Zone 39 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04804 | Zone 39 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04805 | Zone 39 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:04901 | Zone 40 | Zone is defined in CU | 0 | 1
1:04902 | Zone 40 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:04903 | Zone 40 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:04904 | Zone 40 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:04905 | Zone 40 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05001 | Zone 41 | Zone is defined in CU | 0 | 1
1:05002 | Zone 41 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05003 | Zone 41 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05004 | Zone 41 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05005 | Zone 41 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05101 | Zone 42 | Zone is defined in CU | 0 | 1
1:05102 | Zone 42 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05103 | Zone 42 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05104 | Zone 42 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05105 | Zone 42 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05201 | Zone 43 | Zone is defined in CU | 0 | 1
1:05202 | Zone 43 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05203 | Zone 43 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05204 | Zone 43 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05205 | Zone 43 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05301 | Zone 44 | Zone is defined in CU | 0 | 1
1:05302 | Zone 44 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05303 | Zone 44 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05304 | Zone 44 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05305 | Zone 44 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05401 | Zone 45 | Zone is defined in CU | 0 | 1
1:05402 | Zone 45 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05403 | Zone 45 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05404 | Zone 45 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05405 | Zone 45 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05501 | Zone 46 | Zone is defined in CU | 0 | 1
1:05502 | Zone 46 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05503 | Zone 46 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05504 | Zone 46 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05505 | Zone 46 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05601 | Zone 47 | Zone is defined in CU | 0 | 1
1:05602 | Zone 47 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05603 | Zone 47 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05604 | Zone 47 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05605 | Zone 47 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05701 | Zone 48 | Zone is defined in CU | 0 | 1
1:05702 | Zone 48 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05703 | Zone 48 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05704 | Zone 48 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05705 | Zone 48 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05801 | Zone 49 | Zone is defined in CU | 0 | 1
1:05802 | Zone 49 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05803 | Zone 49 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05804 | Zone 49 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05805 | Zone 49 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:05901 | Zone 50 | Zone is defined in CU | 0 | 1
1:05902 | Zone 50 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:05903 | Zone 50 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:05904 | Zone 50 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:05905 | Zone 50 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06001 | Zone 51 | Zone is defined in CU | 0 | 1
1:06002 | Zone 51 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06003 | Zone 51 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06004 | Zone 51 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06005 | Zone 51 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06101 | Zone 52 | Zone is defined in CU | 0 | 1
1:06102 | Zone 52 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06103 | Zone 52 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06104 | Zone 52 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06105 | Zone 52 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06201 | Zone 53 | Zone is defined in CU | 0 | 1
1:06202 | Zone 53 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06203 | Zone 53 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06204 | Zone 53 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06205 | Zone 53 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06301 | Zone 54 | Zone is defined in CU | 0 | 1
1:06302 | Zone 54 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06303 | Zone 54 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06304 | Zone 54 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06305 | Zone 54 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06401 | Zone 55 | Zone is defined in CU | 0 | 1
1:06402 | Zone 55 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06403 | Zone 55 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06404 | Zone 55 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06405 | Zone 55 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06501 | Zone 56 | Zone is defined in CU | 0 | 1
1:06502 | Zone 56 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06503 | Zone 56 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06504 | Zone 56 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06505 | Zone 56 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06601 | Zone 57 | Zone is defined in CU | 0 | 1
1:06602 | Zone 57 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06603 | Zone 57 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06604 | Zone 57 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06605 | Zone 57 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06701 | Zone 58 | Zone is defined in CU | 0 | 1
1:06702 | Zone 58 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06703 | Zone 58 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06704 | Zone 58 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06705 | Zone 58 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06801 | Zone 59 | Zone is defined in CU | 0 | 1
1:06802 | Zone 59 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06803 | Zone 59 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06804 | Zone 59 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06805 | Zone 59 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:06901 | Zone 60 | Zone is defined in CU | 0 | 1
1:06902 | Zone 60 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:06903 | Zone 60 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:06904 | Zone 60 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:06905 | Zone 60 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:07001 | Zone 61 | Zone is defined in CU | 0 | 1
1:07002 | Zone 61 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:07003 | Zone 61 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:07004 | Zone 61 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:07005 | Zone 61 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:07101 | Zone 62 | Zone is defined in CU | 0 | 1
1:07102 | Zone 62 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:07103 | Zone 62 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:07104 | Zone 62 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:07105 | Zone 62 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:07201 | Zone 63 | Zone is defined in CU | 0 | 1
1:07202 | Zone 63 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:07203 | Zone 63 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:07204 | Zone 63 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:07205 | Zone 63 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:07301 | Zone 64 | Zone is defined in CU | 0 | 1
1:07302 | Zone 64 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:07303 | Zone 64 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:07304 | Zone 64 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:07305 | Zone 64 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11001 | Zone 1 | Zone is defined in CU | 0 | 1
1:11002 | Zone 2 | Zone is defined in CU | 0 | 1
1:11003 | Zone 3 | Zone is defined in CU | 0 | 1
1:11004 | Zone 4 | Zone is defined in CU | 0 | 1
1:11005 | Zone 5 | Zone is defined in CU | 0 | 1
1:11006 | Zone 6 | Zone is defined in CU | 0 | 1
1:11007 | Zone 7 | Zone is defined in CU | 0 | 1
1:11008 | Zone 8 | Zone is defined in CU | 0 | 1
1:11009 | Zone 9 | Zone is defined in CU | 0 | 1
1:11010 | Zone 10 | Zone is defined in CU | 0 | 1
1:11011 | Zone 11 | Zone is defined in CU | 0 | 1
1:11012 | Zone 12 | Zone is defined in CU | 0 | 1
1:11013 | Zone 13 | Zone is defined in CU | 0 | 1
1:11014 | Zone 14 | Zone is defined in CU | 0 | 1
1:11015 | Zone 15 | Zone is defined in CU | 0 | 1
1:11016 | Zone 16 | Zone is defined in CU | 0 | 1
1:11017 | Zone 17 | Zone is defined in CU | 0 | 1
1:11018 | Zone 18 | Zone is defined in CU | 0 | 1
1:11019 | Zone 19 | Zone is defined in CU | 0 | 1
1:11020 | Zone 20 | Zone is defined in CU | 0 | 1
1:11021 | Zone 21 | Zone is defined in CU | 0 | 1
1:11022 | Zone 22 | Zone is defined in CU | 0 | 1
1:11023 | Zone 23 | Zone is defined in CU | 0 | 1
1:11024 | Zone 24 | Zone is defined in CU | 0 | 1
1:11025 | Zone 25 | Zone is defined in CU | 0 | 1
1:11026 | Zone 26 | Zone is defined in CU | 0 | 1
1:11027 | Zone 27 | Zone is defined in CU | 0 | 1
1:11028 | Zone 28 | Zone is defined in CU | 0 | 1
1:11029 | Zone 29 | Zone is defined in CU | 0 | 1
1:11030 | Zone 30 | Zone is defined in CU | 0 | 1
1:11031 | Zone 31 | Zone is defined in CU | 0 | 1
1:11032 | Zone 32 | Zone is defined in CU | 0 | 1
1:11033 | Zone 33 | Zone is defined in CU | 0 | 1
1:11034 | Zone 34 | Zone is defined in CU | 0 | 1
1:11035 | Zone 35 | Zone is defined in CU | 0 | 1
1:11036 | Zone 36 | Zone is defined in CU | 0 | 1
1:11037 | Zone 37 | Zone is defined in CU | 0 | 1
1:11038 | Zone 38 | Zone is defined in CU | 0 | 1
1:11039 | Zone 39 | Zone is defined in CU | 0 | 1
1:11040 | Zone 40 | Zone is defined in CU | 0 | 1
1:11041 | Zone 41 | Zone is defined in CU | 0 | 1
1:11042 | Zone 42 | Zone is defined in CU | 0 | 1
1:11043 | Zone 43 | Zone is defined in CU | 0 | 1
1:11044 | Zone 44 | Zone is defined in CU | 0 | 1
1:11045 | Zone 45 | Zone is defined in CU | 0 | 1
1:11046 | Zone 46 | Zone is defined in CU | 0 | 1
1:11047 | Zone 47 | Zone is defined in CU | 0 | 1
1:11048 | Zone 48 | Zone is defined in CU | 0 | 1
1:11049 | Zone 49 | Zone is defined in CU | 0 | 1
1:11050 | Zone 50 | Zone is defined in CU | 0 | 1
1:11051 | Zone 51 | Zone is defined in CU | 0 | 1
1:11052 | Zone 52 | Zone is defined in CU | 0 | 1
1:11053 | Zone 53 | Zone is defined in CU | 0 | 1
1:11054 | Zone 54 | Zone is defined in CU | 0 | 1
1:11055 | Zone 55 | Zone is defined in CU | 0 | 1
1:11056 | Zone 56 | Zone is defined in CU | 0 | 1
1:11057 | Zone 57 | Zone is defined in CU | 0 | 1
1:11058 | Zone 58 | Zone is defined in CU | 0 | 1
1:11059 | Zone 59 | Zone is defined in CU | 0 | 1
1:11060 | Zone 60 | Zone is defined in CU | 0 | 1
1:11061 | Zone 61 | Zone is defined in CU | 0 | 1
1:11062 | Zone 62 | Zone is defined in CU | 0 | 1
1:11063 | Zone 63 | Zone is defined in CU | 0 | 1
1:11064 | Zone 64 | Zone is defined in CU | 0 | 1
1:11065 | Zone 1 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11066 | Zone 2 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11067 | Zone 3 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11068 | Zone 4 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11069 | Zone 5 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11070 | Zone 6 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11071 | Zone 7 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11072 | Zone 8 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11073 | Zone 9 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11074 | Zone 10 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11075 | Zone 11 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11076 | Zone 12 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11077 | Zone 13 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11078 | Zone 14 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11079 | Zone 15 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11080 | Zone 16 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11081 | Zone 17 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11082 | Zone 18 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11083 | Zone 19 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11084 | Zone 20 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11085 | Zone 21 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11086 | Zone 22 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11087 | Zone 23 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11088 | Zone 24 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11089 | Zone 25 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11090 | Zone 26 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11091 | Zone 27 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11092 | Zone 28 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11093 | Zone 29 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11094 | Zone 30 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11095 | Zone 31 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11096 | Zone 32 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11097 | Zone 33 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11098 | Zone 34 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11099 | Zone 35 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11100 | Zone 36 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11101 | Zone 37 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11102 | Zone 38 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11103 | Zone 39 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11104 | Zone 40 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11105 | Zone 41 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11106 | Zone 42 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11107 | Zone 43 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11108 | Zone 44 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11109 | Zone 45 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11110 | Zone 46 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11111 | Zone 47 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11112 | Zone 48 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11113 | Zone 49 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11114 | Zone 50 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11115 | Zone 51 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11116 | Zone 52 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11117 | Zone 53 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11118 | Zone 54 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11119 | Zone 55 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11120 | Zone 56 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11121 | Zone 57 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11122 | Zone 58 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11123 | Zone 59 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11124 | Zone 60 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11125 | Zone 61 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11126 | Zone 62 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11127 | Zone 63 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11128 | Zone 64 | Room Unit type - RUR or RUW | 0 | 1 |  | 0 - RUW; 1 - RUR
1:11129 | Zone 1 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11130 | Zone 2 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11131 | Zone 3 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11132 | Zone 4 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11133 | Zone 5 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11134 | Zone 6 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11135 | Zone 7 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11136 | Zone 8 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11137 | Zone 9 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11138 | Zone 10 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11139 | Zone 11 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11140 | Zone 12 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11141 | Zone 13 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11142 | Zone 14 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11143 | Zone 15 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11144 | Zone 16 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11145 | Zone 17 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11146 | Zone 18 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11147 | Zone 19 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11148 | Zone 20 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11149 | Zone 21 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11150 | Zone 22 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11151 | Zone 23 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11152 | Zone 24 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11153 | Zone 25 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11154 | Zone 26 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11155 | Zone 27 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11156 | Zone 28 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11157 | Zone 29 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11158 | Zone 30 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11159 | Zone 31 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11160 | Zone 32 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11161 | Zone 33 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11162 | Zone 34 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11163 | Zone 35 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11164 | Zone 36 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11165 | Zone 37 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11166 | Zone 38 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11167 | Zone 39 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11168 | Zone 40 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11169 | Zone 41 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11170 | Zone 42 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11171 | Zone 43 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11172 | Zone 44 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11173 | Zone 45 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11174 | Zone 46 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11175 | Zone 47 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11176 | Zone 48 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11177 | Zone 49 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11178 | Zone 50 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11179 | Zone 51 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11180 | Zone 52 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11181 | Zone 53 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11182 | Zone 54 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11183 | Zone 55 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11184 | Zone 56 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11185 | Zone 57 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11186 | Zone 58 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11187 | Zone 59 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11188 | Zone 60 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11189 | Zone 61 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11190 | Zone 62 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11191 | Zone 63 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11192 | Zone 64 | Current Week Program Setpoint Mode | 0 | 1 |  | 0 - Comfort, 1 - Economy.
1:11193 | Zone 1 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11194 | Zone 2 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11195 | Zone 3 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11196 | Zone 4 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11197 | Zone 5 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11198 | Zone 6 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11199 | Zone 7 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11200 | Zone 8 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11201 | Zone 9 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11202 | Zone 10 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11203 | Zone 11 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11204 | Zone 12 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11205 | Zone 13 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11206 | Zone 14 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11207 | Zone 15 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11208 | Zone 16 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11209 | Zone 17 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11210 | Zone 18 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11211 | Zone 19 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11212 | Zone 20 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11213 | Zone 21 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11214 | Zone 22 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11215 | Zone 23 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11216 | Zone 24 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11217 | Zone 25 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11218 | Zone 26 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11219 | Zone 27 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11220 | Zone 28 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11221 | Zone 29 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11222 | Zone 30 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11223 | Zone 31 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11224 | Zone 32 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11225 | Zone 33 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11226 | Zone 34 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11227 | Zone 35 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11228 | Zone 36 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11229 | Zone 37 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11230 | Zone 38 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11231 | Zone 39 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11232 | Zone 40 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11233 | Zone 41 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11234 | Zone 42 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11235 | Zone 43 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11236 | Zone 44 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11237 | Zone 45 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11238 | Zone 46 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11239 | Zone 47 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11240 | Zone 48 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11241 | Zone 49 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11242 | Zone 50 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11243 | Zone 51 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11244 | Zone 52 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11245 | Zone 53 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11246 | Zone 54 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11247 | Zone 55 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11248 | Zone 56 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11249 | Zone 57 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11250 | Zone 58 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11251 | Zone 59 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11252 | Zone 60 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11253 | Zone 61 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11254 | Zone 62 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11255 | Zone 63 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11256 | Zone 64 | Heat Status | 0 | 1 |  | 0 - No Heating In Zone, 1 - Heating Active.
1:11257 | Zone 1 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11258 | Zone 2 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11259 | Zone 3 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11260 | Zone 4 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11261 | Zone 5 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11262 | Zone 6 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11263 | Zone 7 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11264 | Zone 8 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11265 | Zone 9 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11266 | Zone 10 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11267 | Zone 11 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11268 | Zone 12 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11269 | Zone 13 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11270 | Zone 14 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11271 | Zone 15 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11272 | Zone 16 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11273 | Zone 17 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11274 | Zone 18 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11275 | Zone 19 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11276 | Zone 20 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11277 | Zone 21 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11278 | Zone 22 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11279 | Zone 23 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11280 | Zone 24 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11281 | Zone 25 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11282 | Zone 26 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11283 | Zone 27 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11284 | Zone 28 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11285 | Zone 29 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11286 | Zone 30 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11287 | Zone 31 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11288 | Zone 32 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11289 | Zone 33 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11290 | Zone 34 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11291 | Zone 35 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11292 | Zone 36 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11293 | Zone 37 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11294 | Zone 38 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11295 | Zone 39 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11296 | Zone 40 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11297 | Zone 41 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11298 | Zone 42 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11299 | Zone 43 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11300 | Zone 44 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11301 | Zone 45 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11302 | Zone 46 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11303 | Zone 47 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11304 | Zone 48 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11305 | Zone 49 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11306 | Zone 50 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11307 | Zone 51 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11308 | Zone 52 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11309 | Zone 53 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11310 | Zone 54 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11311 | Zone 55 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11312 | Zone 56 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11313 | Zone 57 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11314 | Zone 58 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11315 | Zone 59 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11316 | Zone 60 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11317 | Zone 61 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11318 | Zone 62 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11319 | Zone 63 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed
1:11320 | Zone 64 | Bypass allowed by zone | 0 | 1 |  | 0 - Bypass not allowed, 1 - Bypass allowed

## Input Registers
Modbus | Range | Register | Min | Max | Unit | Notes
3:00001 | System | System Mode Override Status | 0 | 2 |  | 0 - no override, use operation mode from zone; 1 - holiday mode; 2 - setback mode
3:00101 | Section 1 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00102 | Section 1 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00103 | Section 1 | Software version | 0 | 0xffff | 0,01
3:00104 | Section 1 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00105 | Section 1 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00106 | Section 1 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00107 | Section 1 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00108 | Section 1 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00109 | Section 1 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00110 | Section 1 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00111 | Section 1 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00112 | Section 1 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00201 | Section 2 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00202 | Section 2 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00203 | Section 2 | Software version | 0 | 0xffff | 0,01
3:00204 | Section 2 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00205 | Section 2 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00206 | Section 2 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00207 | Section 2 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00208 | Section 2 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00209 | Section 2 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00210 | Section 2 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00211 | Section 2 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00212 | Section 2 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00301 | Section 3 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00302 | Section 3 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00303 | Section 3 | Software version | 0 | 0xffff | 0,01
3:00304 | Section 3 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00305 | Section 3 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00306 | Section 3 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00307 | Section 3 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00308 | Section 3 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00309 | Section 3 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00310 | Section 3 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00311 | Section 3 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00312 | Section 3 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00401 | Section 4 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00402 | Section 4 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00403 | Section 4 | Software version | 0 | 0xffff | 0,01
3:00404 | Section 4 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00405 | Section 4 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00406 | Section 4 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00407 | Section 4 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00408 | Section 4 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00409 | Section 4 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00410 | Section 4 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00411 | Section 4 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00412 | Section 4 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00501 | Section 5 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00502 | Section 5 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00503 | Section 5 | Software version | 0 | 0xffff | 0,01
3:00504 | Section 5 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00505 | Section 5 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00506 | Section 5 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00507 | Section 5 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00508 | Section 5 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00509 | Section 5 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00510 | Section 5 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00511 | Section 5 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00512 | Section 5 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00601 | Section 6 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00602 | Section 6 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00603 | Section 6 | Software version | 0 | 0xffff | 0,01
3:00604 | Section 6 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00605 | Section 6 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00606 | Section 6 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00607 | Section 6 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00608 | Section 6 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00609 | Section 6 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00610 | Section 6 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00611 | Section 6 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00612 | Section 6 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00701 | Section 7 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00702 | Section 7 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00703 | Section 7 | Software version | 0 | 0xffff | 0,01
3:00704 | Section 7 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00705 | Section 7 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00706 | Section 7 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00707 | Section 7 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00708 | Section 7 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00709 | Section 7 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00710 | Section 7 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00711 | Section 7 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00712 | Section 7 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:00801 | Section 8 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:00802 | Section 8 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:00803 | Section 8 | Software version | 0 | 0xffff | 0,01
3:00804 | Section 8 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00805 | Section 8 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00806 | Section 8 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00807 | Section 8 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00808 | Section 8 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00809 | Section 8 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00810 | Section 8 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00811 | Section 8 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:00812 | Section 8 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:01001 | Zone 1 | RU software version | 0 | 0xffff | 0,01
3:01002 | Zone 1 | Room Temp | 0 | 5000 | 0,01°C
3:01003 | Zone 1 | Floor Temp | 0 | 5000 | 0,01°C
3:01004 | Zone 1 | Battery Level | 0 | 100 | %
3:01005 | Zone 1 | Link Quality | 0 | 100
3:01006 | Zone 1 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01007 | Zone 1 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01008 | Zone 1 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01009 | Zone 1 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01010 | Zone 1 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01101 | Zone 2 | RU software version | 0 | 0xffff | 0,01
3:01102 | Zone 2 | Room Temp | 0 | 5000 | 0,01°C
3:01103 | Zone 2 | Floor Temp | 0 | 5000 | 0,01°C
3:01104 | Zone 2 | Battery Level | 0 | 100 | %
3:01105 | Zone 2 | Link Quality | 0 | 100
3:01106 | Zone 2 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01107 | Zone 2 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01108 | Zone 2 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01109 | Zone 2 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01110 | Zone 2 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01201 | Zone 3 | RU software version | 0 | 0xffff | 0,01
3:01202 | Zone 3 | Room Temp | 0 | 5000 | 0,01°C
3:01203 | Zone 3 | Floor Temp | 0 | 5000 | 0,01°C
3:01204 | Zone 3 | Battery Level | 0 | 100 | %
3:01205 | Zone 3 | Link Quality | 0 | 100
3:01206 | Zone 3 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01207 | Zone 3 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01208 | Zone 3 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01209 | Zone 3 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01210 | Zone 3 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01301 | Zone 4 | RU software version | 0 | 0xffff | 0,01
3:01302 | Zone 4 | Room Temp | 0 | 5000 | 0,01°C
3:01303 | Zone 4 | Floor Temp | 0 | 5000 | 0,01°C
3:01304 | Zone 4 | Battery Level | 0 | 100 | %
3:01305 | Zone 4 | Link Quality | 0 | 100
3:01306 | Zone 4 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01307 | Zone 4 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01308 | Zone 4 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01309 | Zone 4 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01310 | Zone 4 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01401 | Zone 5 | RU software version | 0 | 0xffff | 0,01
3:01402 | Zone 5 | Room Temp | 0 | 5000 | 0,01°C
3:01403 | Zone 5 | Floor Temp | 0 | 5000 | 0,01°C
3:01404 | Zone 5 | Battery Level | 0 | 100 | %
3:01405 | Zone 5 | Link Quality | 0 | 100
3:01406 | Zone 5 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01407 | Zone 5 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01408 | Zone 5 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01409 | Zone 5 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01410 | Zone 5 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01501 | Zone 6 | RU software version | 0 | 0xffff | 0,01
3:01502 | Zone 6 | Room Temp | 0 | 5000 | 0,01°C
3:01503 | Zone 6 | Floor Temp | 0 | 5000 | 0,01°C
3:01504 | Zone 6 | Battery Level | 0 | 100 | %
3:01505 | Zone 6 | Link Quality | 0 | 100
3:01506 | Zone 6 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01507 | Zone 6 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01508 | Zone 6 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01509 | Zone 6 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01510 | Zone 6 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01601 | Zone 7 | RU software version | 0 | 0xffff | 0,01
3:01602 | Zone 7 | Room Temp | 0 | 5000 | 0,01°C
3:01603 | Zone 7 | Floor Temp | 0 | 5000 | 0,01°C
3:01604 | Zone 7 | Battery Level | 0 | 100 | %
3:01605 | Zone 7 | Link Quality | 0 | 100
3:01606 | Zone 7 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01607 | Zone 7 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01608 | Zone 7 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01609 | Zone 7 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01610 | Zone 7 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01701 | Zone 8 | RU software version | 0 | 0xffff | 0,01
3:01702 | Zone 8 | Room Temp | 0 | 5000 | 0,01°C
3:01703 | Zone 8 | Floor Temp | 0 | 5000 | 0,01°C
3:01704 | Zone 8 | Battery Level | 0 | 100 | %
3:01705 | Zone 8 | Link Quality | 0 | 100
3:01706 | Zone 8 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01707 | Zone 8 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01708 | Zone 8 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01709 | Zone 8 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01710 | Zone 8 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01801 | Zone 9 | RU software version | 0 | 0xffff | 0,01
3:01802 | Zone 9 | Room Temp | 0 | 5000 | 0,01°C
3:01803 | Zone 9 | Floor Temp | 0 | 5000 | 0,01°C
3:01804 | Zone 9 | Battery Level | 0 | 100 | %
3:01805 | Zone 9 | Link Quality | 0 | 100
3:01806 | Zone 9 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01807 | Zone 9 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01808 | Zone 9 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01809 | Zone 9 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01810 | Zone 9 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:01901 | Zone 10 | RU software version | 0 | 0xffff | 0,01
3:01902 | Zone 10 | Room Temp | 0 | 5000 | 0,01°C
3:01903 | Zone 10 | Floor Temp | 0 | 5000 | 0,01°C
3:01904 | Zone 10 | Battery Level | 0 | 100 | %
3:01905 | Zone 10 | Link Quality | 0 | 100
3:01906 | Zone 10 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:01907 | Zone 10 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:01908 | Zone 10 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:01909 | Zone 10 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:01910 | Zone 10 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02001 | Zone 11 | RU software version | 0 | 0xffff | 0,01
3:02002 | Zone 11 | Room Temp | 0 | 5000 | 0,01°C
3:02003 | Zone 11 | Floor Temp | 0 | 5000 | 0,01°C
3:02004 | Zone 11 | Battery Level | 0 | 100 | %
3:02005 | Zone 11 | Link Quality | 0 | 100
3:02006 | Zone 11 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02007 | Zone 11 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02008 | Zone 11 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02009 | Zone 11 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02010 | Zone 11 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02101 | Zone 12 | RU software version | 0 | 0xffff | 0,01
3:02102 | Zone 12 | Room Temp | 0 | 5000 | 0,01°C
3:02103 | Zone 12 | Floor Temp | 0 | 5000 | 0,01°C
3:02104 | Zone 12 | Battery Level | 0 | 100 | %
3:02105 | Zone 12 | Link Quality | 0 | 100
3:02106 | Zone 12 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02107 | Zone 12 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02108 | Zone 12 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02109 | Zone 12 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02110 | Zone 12 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02201 | Zone 13 | RU software version | 0 | 0xffff | 0,01
3:02202 | Zone 13 | Room Temp | 0 | 5000 | 0,01°C
3:02203 | Zone 13 | Floor Temp | 0 | 5000 | 0,01°C
3:02204 | Zone 13 | Battery Level | 0 | 100 | %
3:02205 | Zone 13 | Link Quality | 0 | 100
3:02206 | Zone 13 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02207 | Zone 13 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02208 | Zone 13 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02209 | Zone 13 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02210 | Zone 13 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02301 | Zone 14 | RU software version | 0 | 0xffff | 0,01
3:02302 | Zone 14 | Room Temp | 0 | 5000 | 0,01°C
3:02303 | Zone 14 | Floor Temp | 0 | 5000 | 0,01°C
3:02304 | Zone 14 | Battery Level | 0 | 100 | %
3:02305 | Zone 14 | Link Quality | 0 | 100
3:02306 | Zone 14 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02307 | Zone 14 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02308 | Zone 14 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02309 | Zone 14 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02310 | Zone 14 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02401 | Zone 15 | RU software version | 0 | 0xffff | 0,01
3:02402 | Zone 15 | Room Temp | 0 | 5000 | 0,01°C
3:02403 | Zone 15 | Floor Temp | 0 | 5000 | 0,01°C
3:02404 | Zone 15 | Battery Level | 0 | 100 | %
3:02405 | Zone 15 | Link Quality | 0 | 100
3:02406 | Zone 15 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02407 | Zone 15 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02408 | Zone 15 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02409 | Zone 15 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02410 | Zone 15 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02501 | Zone 16 | RU software version | 0 | 0xffff | 0,01
3:02502 | Zone 16 | Room Temp | 0 | 5000 | 0,01°C
3:02503 | Zone 16 | Floor Temp | 0 | 5000 | 0,01°C
3:02504 | Zone 16 | Battery Level | 0 | 100 | %
3:02505 | Zone 16 | Link Quality | 0 | 100
3:02506 | Zone 16 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02507 | Zone 16 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02508 | Zone 16 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02509 | Zone 16 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02510 | Zone 16 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02601 | Zone 17 | RU software version | 0 | 0xffff | 0,01
3:02602 | Zone 17 | Room Temp | 0 | 5000 | 0,01°C
3:02603 | Zone 17 | Floor Temp | 0 | 5000 | 0,01°C
3:02604 | Zone 17 | Battery Level | 0 | 100 | %
3:02605 | Zone 17 | Link Quality | 0 | 100
3:02606 | Zone 17 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02607 | Zone 17 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02608 | Zone 17 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02609 | Zone 17 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02610 | Zone 17 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02701 | Zone 18 | RU software version | 0 | 0xffff | 0,01
3:02702 | Zone 18 | Room Temp | 0 | 5000 | 0,01°C
3:02703 | Zone 18 | Floor Temp | 0 | 5000 | 0,01°C
3:02704 | Zone 18 | Battery Level | 0 | 100 | %
3:02705 | Zone 18 | Link Quality | 0 | 100
3:02706 | Zone 18 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02707 | Zone 18 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02708 | Zone 18 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02709 | Zone 18 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02710 | Zone 18 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02801 | Zone 19 | RU software version | 0 | 0xffff | 0,01
3:02802 | Zone 19 | Room Temp | 0 | 5000 | 0,01°C
3:02803 | Zone 19 | Floor Temp | 0 | 5000 | 0,01°C
3:02804 | Zone 19 | Battery Level | 0 | 100 | %
3:02805 | Zone 19 | Link Quality | 0 | 100
3:02806 | Zone 19 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02807 | Zone 19 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02808 | Zone 19 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02809 | Zone 19 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02810 | Zone 19 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:02901 | Zone 20 | RU software version | 0 | 0xffff | 0,01
3:02902 | Zone 20 | Room Temp | 0 | 5000 | 0,01°C
3:02903 | Zone 20 | Floor Temp | 0 | 5000 | 0,01°C
3:02904 | Zone 20 | Battery Level | 0 | 100 | %
3:02905 | Zone 20 | Link Quality | 0 | 100
3:02906 | Zone 20 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:02907 | Zone 20 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:02908 | Zone 20 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:02909 | Zone 20 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:02910 | Zone 20 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03001 | Zone 21 | RU software version | 0 | 0xffff | 0,01
3:03002 | Zone 21 | Room Temp | 0 | 5000 | 0,01°C
3:03003 | Zone 21 | Floor Temp | 0 | 5000 | 0,01°C
3:03004 | Zone 21 | Battery Level | 0 | 100 | %
3:03005 | Zone 21 | Link Quality | 0 | 100
3:03006 | Zone 21 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03007 | Zone 21 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03008 | Zone 21 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03009 | Zone 21 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03010 | Zone 21 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03101 | Zone 22 | RU software version | 0 | 0xffff | 0,01
3:03102 | Zone 22 | Room Temp | 0 | 5000 | 0,01°C
3:03103 | Zone 22 | Floor Temp | 0 | 5000 | 0,01°C
3:03104 | Zone 22 | Battery Level | 0 | 100 | %
3:03105 | Zone 22 | Link Quality | 0 | 100
3:03106 | Zone 22 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03107 | Zone 22 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03108 | Zone 22 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03109 | Zone 22 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03110 | Zone 22 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03201 | Zone 23 | RU software version | 0 | 0xffff | 0,01
3:03202 | Zone 23 | Room Temp | 0 | 5000 | 0,01°C
3:03203 | Zone 23 | Floor Temp | 0 | 5000 | 0,01°C
3:03204 | Zone 23 | Battery Level | 0 | 100 | %
3:03205 | Zone 23 | Link Quality | 0 | 100
3:03206 | Zone 23 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03207 | Zone 23 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03208 | Zone 23 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03209 | Zone 23 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03210 | Zone 23 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03301 | Zone 24 | RU software version | 0 | 0xffff | 0,01
3:03302 | Zone 24 | Room Temp | 0 | 5000 | 0,01°C
3:03303 | Zone 24 | Floor Temp | 0 | 5000 | 0,01°C
3:03304 | Zone 24 | Battery Level | 0 | 100 | %
3:03305 | Zone 24 | Link Quality | 0 | 100
3:03306 | Zone 24 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03307 | Zone 24 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03308 | Zone 24 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03309 | Zone 24 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03310 | Zone 24 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03401 | Zone 25 | RU software version | 0 | 0xffff | 0,01
3:03402 | Zone 25 | Room Temp | 0 | 5000 | 0,01°C
3:03403 | Zone 25 | Floor Temp | 0 | 5000 | 0,01°C
3:03404 | Zone 25 | Battery Level | 0 | 100 | %
3:03405 | Zone 25 | Link Quality | 0 | 100
3:03406 | Zone 25 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03407 | Zone 25 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03408 | Zone 25 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03409 | Zone 25 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03410 | Zone 25 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03501 | Zone 26 | RU software version | 0 | 0xffff | 0,01
3:03502 | Zone 26 | Room Temp | 0 | 5000 | 0,01°C
3:03503 | Zone 26 | Floor Temp | 0 | 5000 | 0,01°C
3:03504 | Zone 26 | Battery Level | 0 | 100 | %
3:03505 | Zone 26 | Link Quality | 0 | 100
3:03506 | Zone 26 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03507 | Zone 26 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03508 | Zone 26 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03509 | Zone 26 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03510 | Zone 26 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03601 | Zone 27 | RU software version | 0 | 0xffff | 0,01
3:03602 | Zone 27 | Room Temp | 0 | 5000 | 0,01°C
3:03603 | Zone 27 | Floor Temp | 0 | 5000 | 0,01°C
3:03604 | Zone 27 | Battery Level | 0 | 100 | %
3:03605 | Zone 27 | Link Quality | 0 | 100
3:03606 | Zone 27 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03607 | Zone 27 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03608 | Zone 27 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03609 | Zone 27 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03610 | Zone 27 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03701 | Zone 28 | RU software version | 0 | 0xffff | 0,01
3:03702 | Zone 28 | Room Temp | 0 | 5000 | 0,01°C
3:03703 | Zone 28 | Floor Temp | 0 | 5000 | 0,01°C
3:03704 | Zone 28 | Battery Level | 0 | 100 | %
3:03705 | Zone 28 | Link Quality | 0 | 100
3:03706 | Zone 28 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03707 | Zone 28 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03708 | Zone 28 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03709 | Zone 28 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03710 | Zone 28 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03801 | Zone 29 | RU software version | 0 | 0xffff | 0,01
3:03802 | Zone 29 | Room Temp | 0 | 5000 | 0,01°C
3:03803 | Zone 29 | Floor Temp | 0 | 5000 | 0,01°C
3:03804 | Zone 29 | Battery Level | 0 | 100 | %
3:03805 | Zone 29 | Link Quality | 0 | 100
3:03806 | Zone 29 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03807 | Zone 29 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03808 | Zone 29 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03809 | Zone 29 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03810 | Zone 29 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:03901 | Zone 30 | RU software version | 0 | 0xffff | 0,01
3:03902 | Zone 30 | Room Temp | 0 | 5000 | 0,01°C
3:03903 | Zone 30 | Floor Temp | 0 | 5000 | 0,01°C
3:03904 | Zone 30 | Battery Level | 0 | 100 | %
3:03905 | Zone 30 | Link Quality | 0 | 100
3:03906 | Zone 30 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:03907 | Zone 30 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:03908 | Zone 30 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:03909 | Zone 30 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:03910 | Zone 30 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04001 | Zone 31 | RU software version | 0 | 0xffff | 0,01
3:04002 | Zone 31 | Room Temp | 0 | 5000 | 0,01°C
3:04003 | Zone 31 | Floor Temp | 0 | 5000 | 0,01°C
3:04004 | Zone 31 | Battery Level | 0 | 100 | %
3:04005 | Zone 31 | Link Quality | 0 | 100
3:04006 | Zone 31 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04007 | Zone 31 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04008 | Zone 31 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04009 | Zone 31 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04010 | Zone 31 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04101 | Zone 32 | RU software version | 0 | 0xffff | 0,01
3:04102 | Zone 32 | Room Temp | 0 | 5000 | 0,01°C
3:04103 | Zone 32 | Floor Temp | 0 | 5000 | 0,01°C
3:04104 | Zone 32 | Battery Level | 0 | 100 | %
3:04105 | Zone 32 | Link Quality | 0 | 100
3:04106 | Zone 32 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04107 | Zone 32 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04108 | Zone 32 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04109 | Zone 32 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04110 | Zone 32 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04201 | Zone 33 | RU software version | 0 | 0xffff | 0,01
3:04202 | Zone 33 | Room Temp | 0 | 5000 | 0,01°C
3:04203 | Zone 33 | Floor Temp | 0 | 5000 | 0,01°C
3:04204 | Zone 33 | Battery Level | 0 | 100 | %
3:04205 | Zone 33 | Link Quality | 0 | 100
3:04206 | Zone 33 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04207 | Zone 33 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04208 | Zone 33 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04209 | Zone 33 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04210 | Zone 33 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04301 | Zone 34 | RU software version | 0 | 0xffff | 0,01
3:04302 | Zone 34 | Room Temp | 0 | 5000 | 0,01°C
3:04303 | Zone 34 | Floor Temp | 0 | 5000 | 0,01°C
3:04304 | Zone 34 | Battery Level | 0 | 100 | %
3:04305 | Zone 34 | Link Quality | 0 | 100
3:04306 | Zone 34 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04307 | Zone 34 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04308 | Zone 34 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04309 | Zone 34 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04310 | Zone 34 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04401 | Zone 35 | RU software version | 0 | 0xffff | 0,01
3:04402 | Zone 35 | Room Temp | 0 | 5000 | 0,01°C
3:04403 | Zone 35 | Floor Temp | 0 | 5000 | 0,01°C
3:04404 | Zone 35 | Battery Level | 0 | 100 | %
3:04405 | Zone 35 | Link Quality | 0 | 100
3:04406 | Zone 35 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04407 | Zone 35 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04408 | Zone 35 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04409 | Zone 35 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04410 | Zone 35 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04501 | Zone 36 | RU software version | 0 | 0xffff | 0,01
3:04502 | Zone 36 | Room Temp | 0 | 5000 | 0,01°C
3:04503 | Zone 36 | Floor Temp | 0 | 5000 | 0,01°C
3:04504 | Zone 36 | Battery Level | 0 | 100 | %
3:04505 | Zone 36 | Link Quality | 0 | 100
3:04506 | Zone 36 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04507 | Zone 36 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04508 | Zone 36 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04509 | Zone 36 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04510 | Zone 36 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04601 | Zone 37 | RU software version | 0 | 0xffff | 0,01
3:04602 | Zone 37 | Room Temp | 0 | 5000 | 0,01°C
3:04603 | Zone 37 | Floor Temp | 0 | 5000 | 0,01°C
3:04604 | Zone 37 | Battery Level | 0 | 100 | %
3:04605 | Zone 37 | Link Quality | 0 | 100
3:04606 | Zone 37 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04607 | Zone 37 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04608 | Zone 37 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04609 | Zone 37 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04610 | Zone 37 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04701 | Zone 38 | RU software version | 0 | 0xffff | 0,01
3:04702 | Zone 38 | Room Temp | 0 | 5000 | 0,01°C
3:04703 | Zone 38 | Floor Temp | 0 | 5000 | 0,01°C
3:04704 | Zone 38 | Battery Level | 0 | 100 | %
3:04705 | Zone 38 | Link Quality | 0 | 100
3:04706 | Zone 38 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04707 | Zone 38 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04708 | Zone 38 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04709 | Zone 38 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04710 | Zone 38 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04801 | Zone 39 | RU software version | 0 | 0xffff | 0,01
3:04802 | Zone 39 | Room Temp | 0 | 5000 | 0,01°C
3:04803 | Zone 39 | Floor Temp | 0 | 5000 | 0,01°C
3:04804 | Zone 39 | Battery Level | 0 | 100 | %
3:04805 | Zone 39 | Link Quality | 0 | 100
3:04806 | Zone 39 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04807 | Zone 39 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04808 | Zone 39 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04809 | Zone 39 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04810 | Zone 39 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:04901 | Zone 40 | RU software version | 0 | 0xffff | 0,01
3:04902 | Zone 40 | Room Temp | 0 | 5000 | 0,01°C
3:04903 | Zone 40 | Floor Temp | 0 | 5000 | 0,01°C
3:04904 | Zone 40 | Battery Level | 0 | 100 | %
3:04905 | Zone 40 | Link Quality | 0 | 100
3:04906 | Zone 40 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:04907 | Zone 40 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:04908 | Zone 40 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:04909 | Zone 40 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:04910 | Zone 40 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05001 | Zone 41 | RU software version | 0 | 0xffff | 0,01
3:05002 | Zone 41 | Room Temp | 0 | 5000 | 0,01°C
3:05003 | Zone 41 | Floor Temp | 0 | 5000 | 0,01°C
3:05004 | Zone 41 | Battery Level | 0 | 100 | %
3:05005 | Zone 41 | Link Quality | 0 | 100
3:05006 | Zone 41 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05007 | Zone 41 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05008 | Zone 41 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05009 | Zone 41 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05010 | Zone 41 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05101 | Zone 42 | RU software version | 0 | 0xffff | 0,01
3:05102 | Zone 42 | Room Temp | 0 | 5000 | 0,01°C
3:05103 | Zone 42 | Floor Temp | 0 | 5000 | 0,01°C
3:05104 | Zone 42 | Battery Level | 0 | 100 | %
3:05105 | Zone 42 | Link Quality | 0 | 100
3:05106 | Zone 42 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05107 | Zone 42 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05108 | Zone 42 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05109 | Zone 42 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05110 | Zone 42 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05201 | Zone 43 | RU software version | 0 | 0xffff | 0,01
3:05202 | Zone 43 | Room Temp | 0 | 5000 | 0,01°C
3:05203 | Zone 43 | Floor Temp | 0 | 5000 | 0,01°C
3:05204 | Zone 43 | Battery Level | 0 | 100 | %
3:05205 | Zone 43 | Link Quality | 0 | 100
3:05206 | Zone 43 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05207 | Zone 43 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05208 | Zone 43 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05209 | Zone 43 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05210 | Zone 43 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05301 | Zone 44 | RU software version | 0 | 0xffff | 0,01
3:05302 | Zone 44 | Room Temp | 0 | 5000 | 0,01°C
3:05303 | Zone 44 | Floor Temp | 0 | 5000 | 0,01°C
3:05304 | Zone 44 | Battery Level | 0 | 100 | %
3:05305 | Zone 44 | Link Quality | 0 | 100
3:05306 | Zone 44 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05307 | Zone 44 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05308 | Zone 44 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05309 | Zone 44 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05310 | Zone 44 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05401 | Zone 45 | RU software version | 0 | 0xffff | 0,01
3:05402 | Zone 45 | Room Temp | 0 | 5000 | 0,01°C
3:05403 | Zone 45 | Floor Temp | 0 | 5000 | 0,01°C
3:05404 | Zone 45 | Battery Level | 0 | 100 | %
3:05405 | Zone 45 | Link Quality | 0 | 100
3:05406 | Zone 45 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05407 | Zone 45 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05408 | Zone 45 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05409 | Zone 45 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05410 | Zone 45 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05501 | Zone 46 | RU software version | 0 | 0xffff | 0,01
3:05502 | Zone 46 | Room Temp | 0 | 5000 | 0,01°C
3:05503 | Zone 46 | Floor Temp | 0 | 5000 | 0,01°C
3:05504 | Zone 46 | Battery Level | 0 | 100 | %
3:05505 | Zone 46 | Link Quality | 0 | 100
3:05506 | Zone 46 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05507 | Zone 46 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05508 | Zone 46 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05509 | Zone 46 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05510 | Zone 46 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05601 | Zone 47 | RU software version | 0 | 0xffff | 0,01
3:05602 | Zone 47 | Room Temp | 0 | 5000 | 0,01°C
3:05603 | Zone 47 | Floor Temp | 0 | 5000 | 0,01°C
3:05604 | Zone 47 | Battery Level | 0 | 100 | %
3:05605 | Zone 47 | Link Quality | 0 | 100
3:05606 | Zone 47 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05607 | Zone 47 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05608 | Zone 47 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05609 | Zone 47 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05610 | Zone 47 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05701 | Zone 48 | RU software version | 0 | 0xffff | 0,01
3:05702 | Zone 48 | Room Temp | 0 | 5000 | 0,01°C
3:05703 | Zone 48 | Floor Temp | 0 | 5000 | 0,01°C
3:05704 | Zone 48 | Battery Level | 0 | 100 | %
3:05705 | Zone 48 | Link Quality | 0 | 100
3:05706 | Zone 48 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05707 | Zone 48 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05708 | Zone 48 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05709 | Zone 48 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05710 | Zone 48 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05801 | Zone 49 | RU software version | 0 | 0xffff | 0,01
3:05802 | Zone 49 | Room Temp | 0 | 5000 | 0,01°C
3:05803 | Zone 49 | Floor Temp | 0 | 5000 | 0,01°C
3:05804 | Zone 49 | Battery Level | 0 | 100 | %
3:05805 | Zone 49 | Link Quality | 0 | 100
3:05806 | Zone 49 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05807 | Zone 49 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05808 | Zone 49 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05809 | Zone 49 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05810 | Zone 49 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:05901 | Zone 50 | RU software version | 0 | 0xffff | 0,01
3:05902 | Zone 50 | Room Temp | 0 | 5000 | 0,01°C
3:05903 | Zone 50 | Floor Temp | 0 | 5000 | 0,01°C
3:05904 | Zone 50 | Battery Level | 0 | 100 | %
3:05905 | Zone 50 | Link Quality | 0 | 100
3:05906 | Zone 50 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:05907 | Zone 50 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:05908 | Zone 50 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:05909 | Zone 50 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:05910 | Zone 50 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06001 | Zone 51 | RU software version | 0 | 0xffff | 0,01
3:06002 | Zone 51 | Room Temp | 0 | 5000 | 0,01°C
3:06003 | Zone 51 | Floor Temp | 0 | 5000 | 0,01°C
3:06004 | Zone 51 | Battery Level | 0 | 100 | %
3:06005 | Zone 51 | Link Quality | 0 | 100
3:06006 | Zone 51 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06007 | Zone 51 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06008 | Zone 51 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06009 | Zone 51 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06010 | Zone 51 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06101 | Zone 52 | RU software version | 0 | 0xffff | 0,01
3:06102 | Zone 52 | Room Temp | 0 | 5000 | 0,01°C
3:06103 | Zone 52 | Floor Temp | 0 | 5000 | 0,01°C
3:06104 | Zone 52 | Battery Level | 0 | 100 | %
3:06105 | Zone 52 | Link Quality | 0 | 100
3:06106 | Zone 52 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06107 | Zone 52 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06108 | Zone 52 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06109 | Zone 52 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06110 | Zone 52 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06201 | Zone 53 | RU software version | 0 | 0xffff | 0,01
3:06202 | Zone 53 | Room Temp | 0 | 5000 | 0,01°C
3:06203 | Zone 53 | Floor Temp | 0 | 5000 | 0,01°C
3:06204 | Zone 53 | Battery Level | 0 | 100 | %
3:06205 | Zone 53 | Link Quality | 0 | 100
3:06206 | Zone 53 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06207 | Zone 53 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06208 | Zone 53 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06209 | Zone 53 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06210 | Zone 53 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06301 | Zone 54 | RU software version | 0 | 0xffff | 0,01
3:06302 | Zone 54 | Room Temp | 0 | 5000 | 0,01°C
3:06303 | Zone 54 | Floor Temp | 0 | 5000 | 0,01°C
3:06304 | Zone 54 | Battery Level | 0 | 100 | %
3:06305 | Zone 54 | Link Quality | 0 | 100
3:06306 | Zone 54 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06307 | Zone 54 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06308 | Zone 54 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06309 | Zone 54 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06310 | Zone 54 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06401 | Zone 55 | RU software version | 0 | 0xffff | 0,01
3:06402 | Zone 55 | Room Temp | 0 | 5000 | 0,01°C
3:06403 | Zone 55 | Floor Temp | 0 | 5000 | 0,01°C
3:06404 | Zone 55 | Battery Level | 0 | 100 | %
3:06405 | Zone 55 | Link Quality | 0 | 100
3:06406 | Zone 55 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06407 | Zone 55 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06408 | Zone 55 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06409 | Zone 55 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06410 | Zone 55 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06501 | Zone 56 | RU software version | 0 | 0xffff | 0,01
3:06502 | Zone 56 | Room Temp | 0 | 5000 | 0,01°C
3:06503 | Zone 56 | Floor Temp | 0 | 5000 | 0,01°C
3:06504 | Zone 56 | Battery Level | 0 | 100 | %
3:06505 | Zone 56 | Link Quality | 0 | 100
3:06506 | Zone 56 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06507 | Zone 56 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06508 | Zone 56 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06509 | Zone 56 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06510 | Zone 56 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06601 | Zone 57 | RU software version | 0 | 0xffff | 0,01
3:06602 | Zone 57 | Room Temp | 0 | 5000 | 0,01°C
3:06603 | Zone 57 | Floor Temp | 0 | 5000 | 0,01°C
3:06604 | Zone 57 | Battery Level | 0 | 100 | %
3:06605 | Zone 57 | Link Quality | 0 | 100
3:06606 | Zone 57 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06607 | Zone 57 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06608 | Zone 57 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06609 | Zone 57 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06610 | Zone 57 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06701 | Zone 58 | RU software version | 0 | 0xffff | 0,01
3:06702 | Zone 58 | Room Temp | 0 | 5000 | 0,01°C
3:06703 | Zone 58 | Floor Temp | 0 | 5000 | 0,01°C
3:06704 | Zone 58 | Battery Level | 0 | 100 | %
3:06705 | Zone 58 | Link Quality | 0 | 100
3:06706 | Zone 58 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06707 | Zone 58 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06708 | Zone 58 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06709 | Zone 58 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06710 | Zone 58 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06801 | Zone 59 | RU software version | 0 | 0xffff | 0,01
3:06802 | Zone 59 | Room Temp | 0 | 5000 | 0,01°C
3:06803 | Zone 59 | Floor Temp | 0 | 5000 | 0,01°C
3:06804 | Zone 59 | Battery Level | 0 | 100 | %
3:06805 | Zone 59 | Link Quality | 0 | 100
3:06806 | Zone 59 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06807 | Zone 59 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06808 | Zone 59 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06809 | Zone 59 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06810 | Zone 59 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:06901 | Zone 60 | RU software version | 0 | 0xffff | 0,01
3:06902 | Zone 60 | Room Temp | 0 | 5000 | 0,01°C
3:06903 | Zone 60 | Floor Temp | 0 | 5000 | 0,01°C
3:06904 | Zone 60 | Battery Level | 0 | 100 | %
3:06905 | Zone 60 | Link Quality | 0 | 100
3:06906 | Zone 60 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:06907 | Zone 60 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:06908 | Zone 60 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:06909 | Zone 60 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:06910 | Zone 60 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:07001 | Zone 61 | RU software version | 0 | 0xffff | 0,01
3:07002 | Zone 61 | Room Temp | 0 | 5000 | 0,01°C
3:07003 | Zone 61 | Floor Temp | 0 | 5000 | 0,01°C
3:07004 | Zone 61 | Battery Level | 0 | 100 | %
3:07005 | Zone 61 | Link Quality | 0 | 100
3:07006 | Zone 61 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:07007 | Zone 61 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:07008 | Zone 61 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:07009 | Zone 61 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:07010 | Zone 61 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:07101 | Zone 62 | RU software version | 0 | 0xffff | 0,01
3:07102 | Zone 62 | Room Temp | 0 | 5000 | 0,01°C
3:07103 | Zone 62 | Floor Temp | 0 | 5000 | 0,01°C
3:07104 | Zone 62 | Battery Level | 0 | 100 | %
3:07105 | Zone 62 | Link Quality | 0 | 100
3:07106 | Zone 62 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:07107 | Zone 62 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:07108 | Zone 62 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:07109 | Zone 62 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:07110 | Zone 62 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:07201 | Zone 63 | RU software version | 0 | 0xffff | 0,01
3:07202 | Zone 63 | Room Temp | 0 | 5000 | 0,01°C
3:07203 | Zone 63 | Floor Temp | 0 | 5000 | 0,01°C
3:07204 | Zone 63 | Battery Level | 0 | 100 | %
3:07205 | Zone 63 | Link Quality | 0 | 100
3:07206 | Zone 63 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:07207 | Zone 63 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:07208 | Zone 63 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:07209 | Zone 63 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:07210 | Zone 63 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:07301 | Zone 64 | RU software version | 0 | 0xffff | 0,01
3:07302 | Zone 64 | Room Temp | 0 | 5000 | 0,01°C
3:07303 | Zone 64 | Floor Temp | 0 | 5000 | 0,01°C
3:07304 | Zone 64 | Battery Level | 0 | 100 | %
3:07305 | Zone 64 | Link Quality | 0 | 100
3:07306 | Zone 64 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:07307 | Zone 64 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:07308 | Zone 64 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:07309 | Zone 64 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:07310 | Zone 64 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:10101 | Section 1 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10102 | Section 2 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10103 | Section 3 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10104 | Section 4 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10105 | Section 5 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10106 | Section 6 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10107 | Section 7 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10108 | Section 8 | CU alarms | 0 | 0xffff |  | bit 0 = actuator error (see actuator alarms) bit 1 = zone error (see zone alarms) bit 2 = CU communication timeout 60min (error 2) bit 3 = cannot switch actuator on, too high current consumption (error 10) bit 4 = duplicate network ID (error 4) bit 5 = data logging error (error 17)
3:10109 | Section 1 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10110 | Section 2 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10111 | Section 3 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10112 | Section 4 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10113 | Section 5 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10114 | Section 6 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10115 | Section 7 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10116 | Section 8 | Cu actuator alarms | 0 | 0xffff |  | 2 bits per actuator, bits 0-1: actuator 0 alarm;bits 14-15: actuator 7 alarm; value 0 - no alarm; 1 = actuator missing (error 11) 2 = acutator short-circuited (error 9) 3 = actuator overload (error 12)
3:10117 | Section 1 | Software version | 0 | 0xffff | 0,01
3:10118 | Section 2 | Software version | 0 | 0xffff | 0,01
3:10119 | Section 3 | Software version | 0 | 0xffff | 0,01
3:10120 | Section 4 | Software version | 0 | 0xffff | 0,01
3:10121 | Section 5 | Software version | 0 | 0xffff | 0,01
3:10122 | Section 6 | Software version | 0 | 0xffff | 0,01
3:10123 | Section 7 | Software version | 0 | 0xffff | 0,01
3:10124 | Section 8 | Software version | 0 | 0xffff | 0,01
3:10125 | Section 1 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10126 | Section 2 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10127 | Section 3 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10128 | Section 4 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10129 | Section 5 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10130 | Section 6 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10131 | Section 7 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10132 | Section 8 | Zone number that uses actuator 1 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10133 | Section 1 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10134 | Section 2 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10135 | Section 3 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10136 | Section 4 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10137 | Section 5 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10138 | Section 6 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10139 | Section 7 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10140 | Section 8 | Zone number that uses actuator 2 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10141 | Section 1 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10142 | Section 2 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10143 | Section 3 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10144 | Section 4 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10145 | Section 5 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10146 | Section 6 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10147 | Section 7 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10148 | Section 8 | Zone number that uses actuator 3 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10149 | Section 1 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10150 | Section 2 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10151 | Section 3 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10152 | Section 4 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10153 | Section 5 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10154 | Section 6 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10155 | Section 7 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10156 | Section 8 | Zone number that uses actuator 4 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10157 | Section 1 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10158 | Section 2 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10159 | Section 3 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10160 | Section 4 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10161 | Section 5 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10162 | Section 6 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10163 | Section 7 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10164 | Section 8 | Zone number that uses actuator 5 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10165 | Section 1 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10166 | Section 2 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10167 | Section 3 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10168 | Section 4 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10169 | Section 5 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10170 | Section 6 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10171 | Section 7 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10172 | Section 8 | Zone number that uses actuator 6 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10173 | Section 1 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10174 | Section 2 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10175 | Section 3 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10176 | Section 4 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10177 | Section 5 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10178 | Section 6 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10179 | Section 7 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10180 | Section 8 | Zone number that uses actuator 7 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10181 | Section 1 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10182 | Section 2 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10183 | Section 3 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10184 | Section 4 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10185 | Section 5 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10186 | Section 6 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10187 | Section 7 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10188 | Section 8 | Zone number that uses actuator 8 | 0 | 8 |  | 0 - actuator not used, 1-8: zone number
3:10189 | Section 1 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10190 | Section 2 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10191 | Section 3 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10192 | Section 4 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10193 | Section 5 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10194 | Section 6 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10195 | Section 7 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:10196 | Section 8 | Bypass currently active in actuators | 0 | 0xffff |  | bit 0 - actuator 1… bit 7 - actuator 8 0 - bypass not active; 1 - bypass active
3:11001 | Zone 1 | RU software version | 0 | 0xffff | 0,01
3:11002 | Zone 2 | RU software version | 0 | 0xffff | 0,01
3:11003 | Zone 3 | RU software version | 0 | 0xffff | 0,01
3:11004 | Zone 4 | RU software version | 0 | 0xffff | 0,01
3:11005 | Zone 5 | RU software version | 0 | 0xffff | 0,01
3:11006 | Zone 6 | RU software version | 0 | 0xffff | 0,01
3:11007 | Zone 7 | RU software version | 0 | 0xffff | 0,01
3:11008 | Zone 8 | RU software version | 0 | 0xffff | 0,01
3:11009 | Zone 9 | RU software version | 0 | 0xffff | 0,01
3:11010 | Zone 10 | RU software version | 0 | 0xffff | 0,01
3:11011 | Zone 11 | RU software version | 0 | 0xffff | 0,01
3:11012 | Zone 12 | RU software version | 0 | 0xffff | 0,01
3:11013 | Zone 13 | RU software version | 0 | 0xffff | 0,01
3:11014 | Zone 14 | RU software version | 0 | 0xffff | 0,01
3:11015 | Zone 15 | RU software version | 0 | 0xffff | 0,01
3:11016 | Zone 16 | RU software version | 0 | 0xffff | 0,01
3:11017 | Zone 17 | RU software version | 0 | 0xffff | 0,01
3:11018 | Zone 18 | RU software version | 0 | 0xffff | 0,01
3:11019 | Zone 19 | RU software version | 0 | 0xffff | 0,01
3:11020 | Zone 20 | RU software version | 0 | 0xffff | 0,01
3:11021 | Zone 21 | RU software version | 0 | 0xffff | 0,01
3:11022 | Zone 22 | RU software version | 0 | 0xffff | 0,01
3:11023 | Zone 23 | RU software version | 0 | 0xffff | 0,01
3:11024 | Zone 24 | RU software version | 0 | 0xffff | 0,01
3:11025 | Zone 25 | RU software version | 0 | 0xffff | 0,01
3:11026 | Zone 26 | RU software version | 0 | 0xffff | 0,01
3:11027 | Zone 27 | RU software version | 0 | 0xffff | 0,01
3:11028 | Zone 28 | RU software version | 0 | 0xffff | 0,01
3:11029 | Zone 29 | RU software version | 0 | 0xffff | 0,01
3:11030 | Zone 30 | RU software version | 0 | 0xffff | 0,01
3:11031 | Zone 31 | RU software version | 0 | 0xffff | 0,01
3:11032 | Zone 32 | RU software version | 0 | 0xffff | 0,01
3:11033 | Zone 33 | RU software version | 0 | 0xffff | 0,01
3:11034 | Zone 34 | RU software version | 0 | 0xffff | 0,01
3:11035 | Zone 35 | RU software version | 0 | 0xffff | 0,01
3:11036 | Zone 36 | RU software version | 0 | 0xffff | 0,01
3:11037 | Zone 37 | RU software version | 0 | 0xffff | 0,01
3:11038 | Zone 38 | RU software version | 0 | 0xffff | 0,01
3:11039 | Zone 39 | RU software version | 0 | 0xffff | 0,01
3:11040 | Zone 40 | RU software version | 0 | 0xffff | 0,01
3:11041 | Zone 41 | RU software version | 0 | 0xffff | 0,01
3:11042 | Zone 42 | RU software version | 0 | 0xffff | 0,01
3:11043 | Zone 43 | RU software version | 0 | 0xffff | 0,01
3:11044 | Zone 44 | RU software version | 0 | 0xffff | 0,01
3:11045 | Zone 45 | RU software version | 0 | 0xffff | 0,01
3:11046 | Zone 46 | RU software version | 0 | 0xffff | 0,01
3:11047 | Zone 47 | RU software version | 0 | 0xffff | 0,01
3:11048 | Zone 48 | RU software version | 0 | 0xffff | 0,01
3:11049 | Zone 49 | RU software version | 0 | 0xffff | 0,01
3:11050 | Zone 50 | RU software version | 0 | 0xffff | 0,01
3:11051 | Zone 51 | RU software version | 0 | 0xffff | 0,01
3:11052 | Zone 52 | RU software version | 0 | 0xffff | 0,01
3:11053 | Zone 53 | RU software version | 0 | 0xffff | 0,01
3:11054 | Zone 54 | RU software version | 0 | 0xffff | 0,01
3:11055 | Zone 55 | RU software version | 0 | 0xffff | 0,01
3:11056 | Zone 56 | RU software version | 0 | 0xffff | 0,01
3:11057 | Zone 57 | RU software version | 0 | 0xffff | 0,01
3:11058 | Zone 58 | RU software version | 0 | 0xffff | 0,01
3:11059 | Zone 59 | RU software version | 0 | 0xffff | 0,01
3:11060 | Zone 60 | RU software version | 0 | 0xffff | 0,01
3:11061 | Zone 61 | RU software version | 0 | 0xffff | 0,01
3:11062 | Zone 62 | RU software version | 0 | 0xffff | 0,01
3:11063 | Zone 63 | RU software version | 0 | 0xffff | 0,01
3:11064 | Zone 64 | RU software version | 0 | 0xffff | 0,01
3:11065 | Zone 1 | Room Temp | 0 | 5000 | 0,01°C
3:11066 | Zone 2 | Room Temp | 0 | 5000 | 0,01°C
3:11067 | Zone 3 | Room Temp | 0 | 5000 | 0,01°C
3:11068 | Zone 4 | Room Temp | 0 | 5000 | 0,01°C
3:11069 | Zone 5 | Room Temp | 0 | 5000 | 0,01°C
3:11070 | Zone 6 | Room Temp | 0 | 5000 | 0,01°C
3:11071 | Zone 7 | Room Temp | 0 | 5000 | 0,01°C
3:11072 | Zone 8 | Room Temp | 0 | 5000 | 0,01°C
3:11073 | Zone 9 | Room Temp | 0 | 5000 | 0,01°C
3:11074 | Zone 10 | Room Temp | 0 | 5000 | 0,01°C
3:11075 | Zone 11 | Room Temp | 0 | 5000 | 0,01°C
3:11076 | Zone 12 | Room Temp | 0 | 5000 | 0,01°C
3:11077 | Zone 13 | Room Temp | 0 | 5000 | 0,01°C
3:11078 | Zone 14 | Room Temp | 0 | 5000 | 0,01°C
3:11079 | Zone 15 | Room Temp | 0 | 5000 | 0,01°C
3:11080 | Zone 16 | Room Temp | 0 | 5000 | 0,01°C
3:11081 | Zone 17 | Room Temp | 0 | 5000 | 0,01°C
3:11082 | Zone 18 | Room Temp | 0 | 5000 | 0,01°C
3:11083 | Zone 19 | Room Temp | 0 | 5000 | 0,01°C
3:11084 | Zone 20 | Room Temp | 0 | 5000 | 0,01°C
3:11085 | Zone 21 | Room Temp | 0 | 5000 | 0,01°C
3:11086 | Zone 22 | Room Temp | 0 | 5000 | 0,01°C
3:11087 | Zone 23 | Room Temp | 0 | 5000 | 0,01°C
3:11088 | Zone 24 | Room Temp | 0 | 5000 | 0,01°C
3:11089 | Zone 25 | Room Temp | 0 | 5000 | 0,01°C
3:11090 | Zone 26 | Room Temp | 0 | 5000 | 0,01°C
3:11091 | Zone 27 | Room Temp | 0 | 5000 | 0,01°C
3:11092 | Zone 28 | Room Temp | 0 | 5000 | 0,01°C
3:11093 | Zone 29 | Room Temp | 0 | 5000 | 0,01°C
3:11094 | Zone 30 | Room Temp | 0 | 5000 | 0,01°C
3:11095 | Zone 31 | Room Temp | 0 | 5000 | 0,01°C
3:11096 | Zone 32 | Room Temp | 0 | 5000 | 0,01°C
3:11097 | Zone 33 | Room Temp | 0 | 5000 | 0,01°C
3:11098 | Zone 34 | Room Temp | 0 | 5000 | 0,01°C
3:11099 | Zone 35 | Room Temp | 0 | 5000 | 0,01°C
3:11100 | Zone 36 | Room Temp | 0 | 5000 | 0,01°C
3:11101 | Zone 37 | Room Temp | 0 | 5000 | 0,01°C
3:11102 | Zone 38 | Room Temp | 0 | 5000 | 0,01°C
3:11103 | Zone 39 | Room Temp | 0 | 5000 | 0,01°C
3:11104 | Zone 40 | Room Temp | 0 | 5000 | 0,01°C
3:11105 | Zone 41 | Room Temp | 0 | 5000 | 0,01°C
3:11106 | Zone 42 | Room Temp | 0 | 5000 | 0,01°C
3:11107 | Zone 43 | Room Temp | 0 | 5000 | 0,01°C
3:11108 | Zone 44 | Room Temp | 0 | 5000 | 0,01°C
3:11109 | Zone 45 | Room Temp | 0 | 5000 | 0,01°C
3:11110 | Zone 46 | Room Temp | 0 | 5000 | 0,01°C
3:11111 | Zone 47 | Room Temp | 0 | 5000 | 0,01°C
3:11112 | Zone 48 | Room Temp | 0 | 5000 | 0,01°C
3:11113 | Zone 49 | Room Temp | 0 | 5000 | 0,01°C
3:11114 | Zone 50 | Room Temp | 0 | 5000 | 0,01°C
3:11115 | Zone 51 | Room Temp | 0 | 5000 | 0,01°C
3:11116 | Zone 52 | Room Temp | 0 | 5000 | 0,01°C
3:11117 | Zone 53 | Room Temp | 0 | 5000 | 0,01°C
3:11118 | Zone 54 | Room Temp | 0 | 5000 | 0,01°C
3:11119 | Zone 55 | Room Temp | 0 | 5000 | 0,01°C
3:11120 | Zone 56 | Room Temp | 0 | 5000 | 0,01°C
3:11121 | Zone 57 | Room Temp | 0 | 5000 | 0,01°C
3:11122 | Zone 58 | Room Temp | 0 | 5000 | 0,01°C
3:11123 | Zone 59 | Room Temp | 0 | 5000 | 0,01°C
3:11124 | Zone 60 | Room Temp | 0 | 5000 | 0,01°C
3:11125 | Zone 61 | Room Temp | 0 | 5000 | 0,01°C
3:11126 | Zone 62 | Room Temp | 0 | 5000 | 0,01°C
3:11127 | Zone 63 | Room Temp | 0 | 5000 | 0,01°C
3:11128 | Zone 64 | Room Temp | 0 | 5000 | 0,01°C
3:11129 | Zone 1 | Floor Temp | 0 | 5000 | 0,01°C
3:11130 | Zone 2 | Floor Temp | 0 | 5000 | 0,01°C
3:11131 | Zone 3 | Floor Temp | 0 | 5000 | 0,01°C
3:11132 | Zone 4 | Floor Temp | 0 | 5000 | 0,01°C
3:11133 | Zone 5 | Floor Temp | 0 | 5000 | 0,01°C
3:11134 | Zone 6 | Floor Temp | 0 | 5000 | 0,01°C
3:11135 | Zone 7 | Floor Temp | 0 | 5000 | 0,01°C
3:11136 | Zone 8 | Floor Temp | 0 | 5000 | 0,01°C
3:11137 | Zone 9 | Floor Temp | 0 | 5000 | 0,01°C
3:11138 | Zone 10 | Floor Temp | 0 | 5000 | 0,01°C
3:11139 | Zone 11 | Floor Temp | 0 | 5000 | 0,01°C
3:11140 | Zone 12 | Floor Temp | 0 | 5000 | 0,01°C
3:11141 | Zone 13 | Floor Temp | 0 | 5000 | 0,01°C
3:11142 | Zone 14 | Floor Temp | 0 | 5000 | 0,01°C
3:11143 | Zone 15 | Floor Temp | 0 | 5000 | 0,01°C
3:11144 | Zone 16 | Floor Temp | 0 | 5000 | 0,01°C
3:11145 | Zone 17 | Floor Temp | 0 | 5000 | 0,01°C
3:11146 | Zone 18 | Floor Temp | 0 | 5000 | 0,01°C
3:11147 | Zone 19 | Floor Temp | 0 | 5000 | 0,01°C
3:11148 | Zone 20 | Floor Temp | 0 | 5000 | 0,01°C
3:11149 | Zone 21 | Floor Temp | 0 | 5000 | 0,01°C
3:11150 | Zone 22 | Floor Temp | 0 | 5000 | 0,01°C
3:11151 | Zone 23 | Floor Temp | 0 | 5000 | 0,01°C
3:11152 | Zone 24 | Floor Temp | 0 | 5000 | 0,01°C
3:11153 | Zone 25 | Floor Temp | 0 | 5000 | 0,01°C
3:11154 | Zone 26 | Floor Temp | 0 | 5000 | 0,01°C
3:11155 | Zone 27 | Floor Temp | 0 | 5000 | 0,01°C
3:11156 | Zone 28 | Floor Temp | 0 | 5000 | 0,01°C
3:11157 | Zone 29 | Floor Temp | 0 | 5000 | 0,01°C
3:11158 | Zone 30 | Floor Temp | 0 | 5000 | 0,01°C
3:11159 | Zone 31 | Floor Temp | 0 | 5000 | 0,01°C
3:11160 | Zone 32 | Floor Temp | 0 | 5000 | 0,01°C
3:11161 | Zone 33 | Floor Temp | 0 | 5000 | 0,01°C
3:11162 | Zone 34 | Floor Temp | 0 | 5000 | 0,01°C
3:11163 | Zone 35 | Floor Temp | 0 | 5000 | 0,01°C
3:11164 | Zone 36 | Floor Temp | 0 | 5000 | 0,01°C
3:11165 | Zone 37 | Floor Temp | 0 | 5000 | 0,01°C
3:11166 | Zone 38 | Floor Temp | 0 | 5000 | 0,01°C
3:11167 | Zone 39 | Floor Temp | 0 | 5000 | 0,01°C
3:11168 | Zone 40 | Floor Temp | 0 | 5000 | 0,01°C
3:11169 | Zone 41 | Floor Temp | 0 | 5000 | 0,01°C
3:11170 | Zone 42 | Floor Temp | 0 | 5000 | 0,01°C
3:11171 | Zone 43 | Floor Temp | 0 | 5000 | 0,01°C
3:11172 | Zone 44 | Floor Temp | 0 | 5000 | 0,01°C
3:11173 | Zone 45 | Floor Temp | 0 | 5000 | 0,01°C
3:11174 | Zone 46 | Floor Temp | 0 | 5000 | 0,01°C
3:11175 | Zone 47 | Floor Temp | 0 | 5000 | 0,01°C
3:11176 | Zone 48 | Floor Temp | 0 | 5000 | 0,01°C
3:11177 | Zone 49 | Floor Temp | 0 | 5000 | 0,01°C
3:11178 | Zone 50 | Floor Temp | 0 | 5000 | 0,01°C
3:11179 | Zone 51 | Floor Temp | 0 | 5000 | 0,01°C
3:11180 | Zone 52 | Floor Temp | 0 | 5000 | 0,01°C
3:11181 | Zone 53 | Floor Temp | 0 | 5000 | 0,01°C
3:11182 | Zone 54 | Floor Temp | 0 | 5000 | 0,01°C
3:11183 | Zone 55 | Floor Temp | 0 | 5000 | 0,01°C
3:11184 | Zone 56 | Floor Temp | 0 | 5000 | 0,01°C
3:11185 | Zone 57 | Floor Temp | 0 | 5000 | 0,01°C
3:11186 | Zone 58 | Floor Temp | 0 | 5000 | 0,01°C
3:11187 | Zone 59 | Floor Temp | 0 | 5000 | 0,01°C
3:11188 | Zone 60 | Floor Temp | 0 | 5000 | 0,01°C
3:11189 | Zone 61 | Floor Temp | 0 | 5000 | 0,01°C
3:11190 | Zone 62 | Floor Temp | 0 | 5000 | 0,01°C
3:11191 | Zone 63 | Floor Temp | 0 | 5000 | 0,01°C
3:11192 | Zone 64 | Floor Temp | 0 | 5000 | 0,01°C
3:11193 | Zone 1 | Battery Level | 0 | 100 | %
3:11194 | Zone 2 | Battery Level | 0 | 100 | %
3:11195 | Zone 3 | Battery Level | 0 | 100 | %
3:11196 | Zone 4 | Battery Level | 0 | 100 | %
3:11197 | Zone 5 | Battery Level | 0 | 100 | %
3:11198 | Zone 6 | Battery Level | 0 | 100 | %
3:11199 | Zone 7 | Battery Level | 0 | 100 | %
3:11200 | Zone 8 | Battery Level | 0 | 100 | %
3:11201 | Zone 9 | Battery Level | 0 | 100 | %
3:11202 | Zone 10 | Battery Level | 0 | 100 | %
3:11203 | Zone 11 | Battery Level | 0 | 100 | %
3:11204 | Zone 12 | Battery Level | 0 | 100 | %
3:11205 | Zone 13 | Battery Level | 0 | 100 | %
3:11206 | Zone 14 | Battery Level | 0 | 100 | %
3:11207 | Zone 15 | Battery Level | 0 | 100 | %
3:11208 | Zone 16 | Battery Level | 0 | 100 | %
3:11209 | Zone 17 | Battery Level | 0 | 100 | %
3:11210 | Zone 18 | Battery Level | 0 | 100 | %
3:11211 | Zone 19 | Battery Level | 0 | 100 | %
3:11212 | Zone 20 | Battery Level | 0 | 100 | %
3:11213 | Zone 21 | Battery Level | 0 | 100 | %
3:11214 | Zone 22 | Battery Level | 0 | 100 | %
3:11215 | Zone 23 | Battery Level | 0 | 100 | %
3:11216 | Zone 24 | Battery Level | 0 | 100 | %
3:11217 | Zone 25 | Battery Level | 0 | 100 | %
3:11218 | Zone 26 | Battery Level | 0 | 100 | %
3:11219 | Zone 27 | Battery Level | 0 | 100 | %
3:11220 | Zone 28 | Battery Level | 0 | 100 | %
3:11221 | Zone 29 | Battery Level | 0 | 100 | %
3:11222 | Zone 30 | Battery Level | 0 | 100 | %
3:11223 | Zone 31 | Battery Level | 0 | 100 | %
3:11224 | Zone 32 | Battery Level | 0 | 100 | %
3:11225 | Zone 33 | Battery Level | 0 | 100 | %
3:11226 | Zone 34 | Battery Level | 0 | 100 | %
3:11227 | Zone 35 | Battery Level | 0 | 100 | %
3:11228 | Zone 36 | Battery Level | 0 | 100 | %
3:11229 | Zone 37 | Battery Level | 0 | 100 | %
3:11230 | Zone 38 | Battery Level | 0 | 100 | %
3:11231 | Zone 39 | Battery Level | 0 | 100 | %
3:11232 | Zone 40 | Battery Level | 0 | 100 | %
3:11233 | Zone 41 | Battery Level | 0 | 100 | %
3:11234 | Zone 42 | Battery Level | 0 | 100 | %
3:11235 | Zone 43 | Battery Level | 0 | 100 | %
3:11236 | Zone 44 | Battery Level | 0 | 100 | %
3:11237 | Zone 45 | Battery Level | 0 | 100 | %
3:11238 | Zone 46 | Battery Level | 0 | 100 | %
3:11239 | Zone 47 | Battery Level | 0 | 100 | %
3:11240 | Zone 48 | Battery Level | 0 | 100 | %
3:11241 | Zone 49 | Battery Level | 0 | 100 | %
3:11242 | Zone 50 | Battery Level | 0 | 100 | %
3:11243 | Zone 51 | Battery Level | 0 | 100 | %
3:11244 | Zone 52 | Battery Level | 0 | 100 | %
3:11245 | Zone 53 | Battery Level | 0 | 100 | %
3:11246 | Zone 54 | Battery Level | 0 | 100 | %
3:11247 | Zone 55 | Battery Level | 0 | 100 | %
3:11248 | Zone 56 | Battery Level | 0 | 100 | %
3:11249 | Zone 57 | Battery Level | 0 | 100 | %
3:11250 | Zone 58 | Battery Level | 0 | 100 | %
3:11251 | Zone 59 | Battery Level | 0 | 100 | %
3:11252 | Zone 60 | Battery Level | 0 | 100 | %
3:11253 | Zone 61 | Battery Level | 0 | 100 | %
3:11254 | Zone 62 | Battery Level | 0 | 100 | %
3:11255 | Zone 63 | Battery Level | 0 | 100 | %
3:11256 | Zone 64 | Battery Level | 0 | 100 | %
3:11257 | Zone 1 | Link Quality | 0 | 100
3:11258 | Zone 2 | Link Quality | 0 | 100
3:11259 | Zone 3 | Link Quality | 0 | 100
3:11260 | Zone 4 | Link Quality | 0 | 100
3:11261 | Zone 5 | Link Quality | 0 | 100
3:11262 | Zone 6 | Link Quality | 0 | 100
3:11263 | Zone 7 | Link Quality | 0 | 100
3:11264 | Zone 8 | Link Quality | 0 | 100
3:11265 | Zone 9 | Link Quality | 0 | 100
3:11266 | Zone 10 | Link Quality | 0 | 100
3:11267 | Zone 11 | Link Quality | 0 | 100
3:11268 | Zone 12 | Link Quality | 0 | 100
3:11269 | Zone 13 | Link Quality | 0 | 100
3:11270 | Zone 14 | Link Quality | 0 | 100
3:11271 | Zone 15 | Link Quality | 0 | 100
3:11272 | Zone 16 | Link Quality | 0 | 100
3:11273 | Zone 17 | Link Quality | 0 | 100
3:11274 | Zone 18 | Link Quality | 0 | 100
3:11275 | Zone 19 | Link Quality | 0 | 100
3:11276 | Zone 20 | Link Quality | 0 | 100
3:11277 | Zone 21 | Link Quality | 0 | 100
3:11278 | Zone 22 | Link Quality | 0 | 100
3:11279 | Zone 23 | Link Quality | 0 | 100
3:11280 | Zone 24 | Link Quality | 0 | 100
3:11281 | Zone 25 | Link Quality | 0 | 100
3:11282 | Zone 26 | Link Quality | 0 | 100
3:11283 | Zone 27 | Link Quality | 0 | 100
3:11284 | Zone 28 | Link Quality | 0 | 100
3:11285 | Zone 29 | Link Quality | 0 | 100
3:11286 | Zone 30 | Link Quality | 0 | 100
3:11287 | Zone 31 | Link Quality | 0 | 100
3:11288 | Zone 32 | Link Quality | 0 | 100
3:11289 | Zone 33 | Link Quality | 0 | 100
3:11290 | Zone 34 | Link Quality | 0 | 100
3:11291 | Zone 35 | Link Quality | 0 | 100
3:11292 | Zone 36 | Link Quality | 0 | 100
3:11293 | Zone 37 | Link Quality | 0 | 100
3:11294 | Zone 38 | Link Quality | 0 | 100
3:11295 | Zone 39 | Link Quality | 0 | 100
3:11296 | Zone 40 | Link Quality | 0 | 100
3:11297 | Zone 41 | Link Quality | 0 | 100
3:11298 | Zone 42 | Link Quality | 0 | 100
3:11299 | Zone 43 | Link Quality | 0 | 100
3:11300 | Zone 44 | Link Quality | 0 | 100
3:11301 | Zone 45 | Link Quality | 0 | 100
3:11302 | Zone 46 | Link Quality | 0 | 100
3:11303 | Zone 47 | Link Quality | 0 | 100
3:11304 | Zone 48 | Link Quality | 0 | 100
3:11305 | Zone 49 | Link Quality | 0 | 100
3:11306 | Zone 50 | Link Quality | 0 | 100
3:11307 | Zone 51 | Link Quality | 0 | 100
3:11308 | Zone 52 | Link Quality | 0 | 100
3:11309 | Zone 53 | Link Quality | 0 | 100
3:11310 | Zone 54 | Link Quality | 0 | 100
3:11311 | Zone 55 | Link Quality | 0 | 100
3:11312 | Zone 56 | Link Quality | 0 | 100
3:11313 | Zone 57 | Link Quality | 0 | 100
3:11314 | Zone 58 | Link Quality | 0 | 100
3:11315 | Zone 59 | Link Quality | 0 | 100
3:11316 | Zone 60 | Link Quality | 0 | 100
3:11317 | Zone 61 | Link Quality | 0 | 100
3:11318 | Zone 62 | Link Quality | 0 | 100
3:11319 | Zone 63 | Link Quality | 0 | 100
3:11320 | Zone 64 | Link Quality | 0 | 100
3:11321 | Zone 1 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11322 | Zone 2 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11323 | Zone 3 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11324 | Zone 4 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11325 | Zone 5 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11326 | Zone 6 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11327 | Zone 7 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11328 | Zone 8 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11329 | Zone 9 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11330 | Zone 10 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11331 | Zone 11 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11332 | Zone 12 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11333 | Zone 13 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11334 | Zone 14 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11335 | Zone 15 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11336 | Zone 16 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11337 | Zone 17 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11338 | Zone 18 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11339 | Zone 19 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11340 | Zone 20 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11341 | Zone 21 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11342 | Zone 22 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11343 | Zone 23 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11344 | Zone 24 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11345 | Zone 25 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11346 | Zone 26 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11347 | Zone 27 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11348 | Zone 28 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11349 | Zone 29 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11350 | Zone 30 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11351 | Zone 31 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11352 | Zone 32 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11353 | Zone 33 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11354 | Zone 34 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11355 | Zone 35 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11356 | Zone 36 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11357 | Zone 37 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11358 | Zone 38 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11359 | Zone 39 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11360 | Zone 40 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11361 | Zone 41 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11362 | Zone 42 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11363 | Zone 43 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11364 | Zone 44 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11365 | Zone 45 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11366 | Zone 46 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11367 | Zone 47 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11368 | Zone 48 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11369 | Zone 49 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11370 | Zone 50 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11371 | Zone 51 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11372 | Zone 52 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11373 | Zone 53 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11374 | Zone 54 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11375 | Zone 55 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11376 | Zone 56 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11377 | Zone 57 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11378 | Zone 58 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11379 | Zone 59 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11380 | Zone 60 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11381 | Zone 61 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11382 | Zone 62 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11383 | Zone 63 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11384 | Zone 64 | Room Unit physical channel | 1 | 8 |  | For RUW the connector used; For RUR channel number?
3:11385 | Zone 1 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11386 | Zone 2 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11387 | Zone 3 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11388 | Zone 4 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11389 | Zone 5 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11390 | Zone 6 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11391 | Zone 7 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11392 | Zone 8 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11393 | Zone 9 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11394 | Zone 10 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11395 | Zone 11 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11396 | Zone 12 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11397 | Zone 13 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11398 | Zone 14 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11399 | Zone 15 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11400 | Zone 16 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11401 | Zone 17 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11402 | Zone 18 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11403 | Zone 19 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11404 | Zone 20 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11405 | Zone 21 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11406 | Zone 22 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11407 | Zone 23 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11408 | Zone 24 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11409 | Zone 25 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11410 | Zone 26 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11411 | Zone 27 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11412 | Zone 28 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11413 | Zone 29 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11414 | Zone 30 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11415 | Zone 31 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11416 | Zone 32 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11417 | Zone 33 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11418 | Zone 34 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11419 | Zone 35 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11420 | Zone 36 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11421 | Zone 37 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11422 | Zone 38 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11423 | Zone 39 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11424 | Zone 40 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11425 | Zone 41 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11426 | Zone 42 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11427 | Zone 43 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11428 | Zone 44 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11429 | Zone 45 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11430 | Zone 46 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11431 | Zone 47 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11432 | Zone 48 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11433 | Zone 49 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11434 | Zone 50 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11435 | Zone 51 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11436 | Zone 52 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11437 | Zone 53 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11438 | Zone 54 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11439 | Zone 55 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11440 | Zone 56 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11441 | Zone 57 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11442 | Zone 58 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11443 | Zone 59 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11444 | Zone 60 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11445 | Zone 61 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11446 | Zone 62 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11447 | Zone 63 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11448 | Zone 64 | PI Regulator Current Room Temp Setpoint | 700 | 4000 | 0,01°C
3:11449 | Zone 1 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11450 | Zone 2 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11451 | Zone 3 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11452 | Zone 4 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11453 | Zone 5 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11454 | Zone 6 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11455 | Zone 7 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11456 | Zone 8 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11457 | Zone 9 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11458 | Zone 10 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11459 | Zone 11 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11460 | Zone 12 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11461 | Zone 13 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11462 | Zone 14 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11463 | Zone 15 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11464 | Zone 16 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11465 | Zone 17 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11466 | Zone 18 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11467 | Zone 19 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11468 | Zone 20 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11469 | Zone 21 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11470 | Zone 22 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11471 | Zone 23 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11472 | Zone 24 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11473 | Zone 25 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11474 | Zone 26 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11475 | Zone 27 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11476 | Zone 28 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11477 | Zone 29 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11478 | Zone 30 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11479 | Zone 31 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11480 | Zone 32 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11481 | Zone 33 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11482 | Zone 34 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11483 | Zone 35 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11484 | Zone 36 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11485 | Zone 37 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11486 | Zone 38 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11487 | Zone 39 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11488 | Zone 40 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11489 | Zone 41 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11490 | Zone 42 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11491 | Zone 43 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11492 | Zone 44 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11493 | Zone 45 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11494 | Zone 46 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11495 | Zone 47 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11496 | Zone 48 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11497 | Zone 49 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11498 | Zone 50 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11499 | Zone 51 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11500 | Zone 52 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11501 | Zone 53 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11502 | Zone 54 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11503 | Zone 55 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11504 | Zone 56 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11505 | Zone 57 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11506 | Zone 58 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11507 | Zone 59 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11508 | Zone 60 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11509 | Zone 61 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11510 | Zone 62 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11511 | Zone 63 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11512 | Zone 64 | PI Regulator Current Floor Temp Setpoint | 700 | 4000 | 0,01°C
3:11513 | Zone 1 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11514 | Zone 2 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11515 | Zone 3 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11516 | Zone 4 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11517 | Zone 5 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11518 | Zone 6 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11519 | Zone 7 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11520 | Zone 8 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11521 | Zone 9 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11522 | Zone 10 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11523 | Zone 11 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11524 | Zone 12 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11525 | Zone 13 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11526 | Zone 14 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11527 | Zone 15 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11528 | Zone 16 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11529 | Zone 17 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11530 | Zone 18 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11531 | Zone 19 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11532 | Zone 20 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11533 | Zone 21 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11534 | Zone 22 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11535 | Zone 23 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11536 | Zone 24 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11537 | Zone 25 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11538 | Zone 26 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11539 | Zone 27 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11540 | Zone 28 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11541 | Zone 29 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11542 | Zone 30 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11543 | Zone 31 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11544 | Zone 32 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11545 | Zone 33 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11546 | Zone 34 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11547 | Zone 35 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11548 | Zone 36 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11549 | Zone 37 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11550 | Zone 38 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11551 | Zone 39 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11552 | Zone 40 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11553 | Zone 41 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11554 | Zone 42 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11555 | Zone 43 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11556 | Zone 44 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11557 | Zone 45 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11558 | Zone 46 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11559 | Zone 47 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11560 | Zone 48 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11561 | Zone 49 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11562 | Zone 50 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11563 | Zone 51 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11564 | Zone 52 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11565 | Zone 53 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11566 | Zone 54 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11567 | Zone 55 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11568 | Zone 56 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11569 | Zone 57 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11570 | Zone 58 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11571 | Zone 59 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11572 | Zone 60 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11573 | Zone 61 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11574 | Zone 62 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11575 | Zone 63 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11576 | Zone 64 | PI Regulation Output | 0 | 100 | % | MIN = 0 MAX = 100 (Firmware prior to v.2.00 used MIN = 0 MAX = 255 HEX)
3:11577 | Zone 1 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11578 | Zone 2 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11579 | Zone 3 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11580 | Zone 4 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11581 | Zone 5 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11582 | Zone 6 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11583 | Zone 7 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11584 | Zone 8 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11585 | Zone 9 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11586 | Zone 10 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11587 | Zone 11 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11588 | Zone 12 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11589 | Zone 13 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11590 | Zone 14 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11591 | Zone 15 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11592 | Zone 16 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11593 | Zone 17 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11594 | Zone 18 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11595 | Zone 19 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11596 | Zone 20 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11597 | Zone 21 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11598 | Zone 22 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11599 | Zone 23 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11600 | Zone 24 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11601 | Zone 25 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11602 | Zone 26 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11603 | Zone 27 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11604 | Zone 28 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11605 | Zone 29 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11606 | Zone 30 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11607 | Zone 31 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11608 | Zone 32 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11609 | Zone 33 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11610 | Zone 34 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11611 | Zone 35 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11612 | Zone 36 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11613 | Zone 37 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11614 | Zone 38 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11615 | Zone 39 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11616 | Zone 40 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11617 | Zone 41 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11618 | Zone 42 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11619 | Zone 43 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11620 | Zone 44 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11621 | Zone 45 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11622 | Zone 46 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11623 | Zone 47 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11624 | Zone 48 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11625 | Zone 49 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11626 | Zone 50 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11627 | Zone 51 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11628 | Zone 52 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11629 | Zone 53 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11630 | Zone 54 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11631 | Zone 55 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11632 | Zone 56 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11633 | Zone 57 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11634 | Zone 58 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11635 | Zone 59 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11636 | Zone 60 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11637 | Zone 61 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11638 | Zone 62 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11639 | Zone 63 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)
3:11640 | Zone 64 | Zone Alarms | 0 | 0xffff |  | bit 0 = Room sensor error (error 15) bit 1 = No Communication between RU-CU for 60 min (error 1) bit 2 = FloorSensor error (error 14) bit 3 = RUW cannot install (unused?) bit 4 = HW Error (error 13) bit 5 = battery low (error 16)

## Holding Registers
Modbus | Range | Register | Min | Max | Unit | Notes
4:00001 | System | Date Year | 2013 | 2099 | year
4:00002 | System | Date Month | 1 | 12 | month
4:00003 | System | Date Day | 1 | 31 | day
4:00004 | System | Time Hour | 0 | 23 | h
4:00005 | System | Time Minute | 0 | 59 | min
4:00006 | System | Time Week Day Number | 1 | 7
4:00007 | System | Holiday Counter | 1 | 2160 | hours | 0 - no override, use operation mode from zone; 1 - holiday mode; 2 - setback mode
4:00008 | System | System Mode Override Set | 0 | 2
4:00901 | Modbus | Modbus slave ID | 1 | 247
4:00902 | Modbus | Modbus baudrate | 0 | 2 |  | 0 - 9600, 1 - 19200, 2 - 38400 bps
4:00903 | Modbus | Modbus parity | 0 | 2 |  | 0 - None, 1 - Odd, 2 - Even
4:00904 | Modbus | Modbus stop bits | 1 | 2
4:01001 | Zone 1 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01002 | Zone 1 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01003 | Zone 1 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01004 | Zone 1 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01005 | Zone 1 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01006 | Zone 1 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01007 | Zone 1 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01008 | Zone 1 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01009 | Zone 1 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01010 | Zone 1 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01011 | Zone 1 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01012 | Zone 1 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01013 | Zone 1 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01014 | Zone 1 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01015 | Zone 1 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01016 | Zone 1 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01017 | Zone 1 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01018 | Zone 1 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01019 | Zone 1 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01020 | Zone 1 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01021 | Zone 1 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01022 | Zone 1 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01023 | Zone 1 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01024 | Zone 1 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01025 | Zone 1 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01026 | Zone 1 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01027 | Zone 1 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01028 | Zone 1 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01029 | Zone 1 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01030 | Zone 1 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01031 | Zone 1 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01032 | Zone 1 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01033 | Zone 1 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01034 | Zone 1 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01035 | Zone 1 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01036 | Zone 1 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01037 | Zone 1 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01038 | Zone 1 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01039 | Zone 1 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01040 | Zone 1 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01041 | Zone 1 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01042 | Zone 1 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01043 | Zone 1 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01044 | Zone 1 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01045 | Zone 1 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01046 | Zone 1 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01047 | Zone 1 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01048 | Zone 1 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01049 | Zone 1 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01050 | Zone 1 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01051 | Zone 1 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01052 | Zone 1 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01053 | Zone 1 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01054 | Zone 1 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01055 | Zone 1 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01056 | Zone 1 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01057 | Zone 1 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01101 | Zone 2 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01102 | Zone 2 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01103 | Zone 2 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01104 | Zone 2 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01105 | Zone 2 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01106 | Zone 2 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01107 | Zone 2 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01108 | Zone 2 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01109 | Zone 2 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01110 | Zone 2 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01111 | Zone 2 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01112 | Zone 2 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01113 | Zone 2 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01114 | Zone 2 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01115 | Zone 2 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01116 | Zone 2 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01117 | Zone 2 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01118 | Zone 2 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01119 | Zone 2 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01120 | Zone 2 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01121 | Zone 2 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01122 | Zone 2 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01123 | Zone 2 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01124 | Zone 2 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01125 | Zone 2 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01126 | Zone 2 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01127 | Zone 2 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01128 | Zone 2 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01129 | Zone 2 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01130 | Zone 2 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01131 | Zone 2 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01132 | Zone 2 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01133 | Zone 2 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01134 | Zone 2 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01135 | Zone 2 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01136 | Zone 2 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01137 | Zone 2 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01138 | Zone 2 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01139 | Zone 2 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01140 | Zone 2 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01141 | Zone 2 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01142 | Zone 2 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01143 | Zone 2 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01144 | Zone 2 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01145 | Zone 2 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01146 | Zone 2 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01147 | Zone 2 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01148 | Zone 2 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01149 | Zone 2 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01150 | Zone 2 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01151 | Zone 2 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01152 | Zone 2 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01153 | Zone 2 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01154 | Zone 2 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01155 | Zone 2 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01156 | Zone 2 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01157 | Zone 2 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01201 | Zone 3 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01202 | Zone 3 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01203 | Zone 3 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01204 | Zone 3 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01205 | Zone 3 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01206 | Zone 3 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01207 | Zone 3 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01208 | Zone 3 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01209 | Zone 3 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01210 | Zone 3 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01211 | Zone 3 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01212 | Zone 3 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01213 | Zone 3 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01214 | Zone 3 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01215 | Zone 3 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01216 | Zone 3 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01217 | Zone 3 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01218 | Zone 3 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01219 | Zone 3 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01220 | Zone 3 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01221 | Zone 3 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01222 | Zone 3 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01223 | Zone 3 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01224 | Zone 3 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01225 | Zone 3 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01226 | Zone 3 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01227 | Zone 3 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01228 | Zone 3 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01229 | Zone 3 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01230 | Zone 3 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01231 | Zone 3 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01232 | Zone 3 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01233 | Zone 3 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01234 | Zone 3 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01235 | Zone 3 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01236 | Zone 3 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01237 | Zone 3 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01238 | Zone 3 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01239 | Zone 3 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01240 | Zone 3 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01241 | Zone 3 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01242 | Zone 3 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01243 | Zone 3 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01244 | Zone 3 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01245 | Zone 3 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01246 | Zone 3 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01247 | Zone 3 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01248 | Zone 3 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01249 | Zone 3 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01250 | Zone 3 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01251 | Zone 3 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01252 | Zone 3 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01253 | Zone 3 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01254 | Zone 3 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01255 | Zone 3 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01256 | Zone 3 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01257 | Zone 3 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01301 | Zone 4 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01302 | Zone 4 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01303 | Zone 4 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01304 | Zone 4 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01305 | Zone 4 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01306 | Zone 4 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01307 | Zone 4 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01308 | Zone 4 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01309 | Zone 4 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01310 | Zone 4 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01311 | Zone 4 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01312 | Zone 4 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01313 | Zone 4 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01314 | Zone 4 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01315 | Zone 4 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01316 | Zone 4 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01317 | Zone 4 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01318 | Zone 4 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01319 | Zone 4 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01320 | Zone 4 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01321 | Zone 4 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01322 | Zone 4 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01323 | Zone 4 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01324 | Zone 4 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01325 | Zone 4 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01326 | Zone 4 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01327 | Zone 4 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01328 | Zone 4 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01329 | Zone 4 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01330 | Zone 4 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01331 | Zone 4 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01332 | Zone 4 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01333 | Zone 4 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01334 | Zone 4 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01335 | Zone 4 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01336 | Zone 4 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01337 | Zone 4 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01338 | Zone 4 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01339 | Zone 4 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01340 | Zone 4 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01341 | Zone 4 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01342 | Zone 4 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01343 | Zone 4 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01344 | Zone 4 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01345 | Zone 4 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01346 | Zone 4 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01347 | Zone 4 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01348 | Zone 4 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01349 | Zone 4 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01350 | Zone 4 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01351 | Zone 4 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01352 | Zone 4 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01353 | Zone 4 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01354 | Zone 4 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01355 | Zone 4 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01356 | Zone 4 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01357 | Zone 4 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01401 | Zone 5 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01402 | Zone 5 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01403 | Zone 5 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01404 | Zone 5 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01405 | Zone 5 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01406 | Zone 5 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01407 | Zone 5 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01408 | Zone 5 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01409 | Zone 5 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01410 | Zone 5 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01411 | Zone 5 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01412 | Zone 5 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01413 | Zone 5 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01414 | Zone 5 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01415 | Zone 5 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01416 | Zone 5 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01417 | Zone 5 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01418 | Zone 5 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01419 | Zone 5 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01420 | Zone 5 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01421 | Zone 5 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01422 | Zone 5 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01423 | Zone 5 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01424 | Zone 5 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01425 | Zone 5 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01426 | Zone 5 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01427 | Zone 5 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01428 | Zone 5 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01429 | Zone 5 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01430 | Zone 5 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01431 | Zone 5 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01432 | Zone 5 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01433 | Zone 5 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01434 | Zone 5 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01435 | Zone 5 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01436 | Zone 5 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01437 | Zone 5 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01438 | Zone 5 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01439 | Zone 5 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01440 | Zone 5 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01441 | Zone 5 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01442 | Zone 5 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01443 | Zone 5 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01444 | Zone 5 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01445 | Zone 5 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01446 | Zone 5 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01447 | Zone 5 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01448 | Zone 5 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01449 | Zone 5 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01450 | Zone 5 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01451 | Zone 5 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01452 | Zone 5 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01453 | Zone 5 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01454 | Zone 5 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01455 | Zone 5 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01456 | Zone 5 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01457 | Zone 5 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01501 | Zone 6 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01502 | Zone 6 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01503 | Zone 6 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01504 | Zone 6 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01505 | Zone 6 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01506 | Zone 6 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01507 | Zone 6 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01508 | Zone 6 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01509 | Zone 6 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01510 | Zone 6 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01511 | Zone 6 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01512 | Zone 6 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01513 | Zone 6 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01514 | Zone 6 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01515 | Zone 6 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01516 | Zone 6 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01517 | Zone 6 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01518 | Zone 6 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01519 | Zone 6 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01520 | Zone 6 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01521 | Zone 6 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01522 | Zone 6 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01523 | Zone 6 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01524 | Zone 6 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01525 | Zone 6 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01526 | Zone 6 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01527 | Zone 6 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01528 | Zone 6 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01529 | Zone 6 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01530 | Zone 6 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01531 | Zone 6 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01532 | Zone 6 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01533 | Zone 6 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01534 | Zone 6 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01535 | Zone 6 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01536 | Zone 6 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01537 | Zone 6 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01538 | Zone 6 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01539 | Zone 6 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01540 | Zone 6 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01541 | Zone 6 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01542 | Zone 6 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01543 | Zone 6 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01544 | Zone 6 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01545 | Zone 6 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01546 | Zone 6 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01547 | Zone 6 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01548 | Zone 6 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01549 | Zone 6 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01550 | Zone 6 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01551 | Zone 6 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01552 | Zone 6 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01553 | Zone 6 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01554 | Zone 6 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01555 | Zone 6 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01556 | Zone 6 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01557 | Zone 6 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01601 | Zone 7 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01602 | Zone 7 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01603 | Zone 7 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01604 | Zone 7 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01605 | Zone 7 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01606 | Zone 7 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01607 | Zone 7 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01608 | Zone 7 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01609 | Zone 7 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01610 | Zone 7 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01611 | Zone 7 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01612 | Zone 7 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01613 | Zone 7 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01614 | Zone 7 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01615 | Zone 7 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01616 | Zone 7 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01617 | Zone 7 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01618 | Zone 7 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01619 | Zone 7 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01620 | Zone 7 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01621 | Zone 7 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01622 | Zone 7 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01623 | Zone 7 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01624 | Zone 7 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01625 | Zone 7 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01626 | Zone 7 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01627 | Zone 7 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01628 | Zone 7 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01629 | Zone 7 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01630 | Zone 7 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01631 | Zone 7 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01632 | Zone 7 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01633 | Zone 7 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01634 | Zone 7 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01635 | Zone 7 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01636 | Zone 7 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01637 | Zone 7 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01638 | Zone 7 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01639 | Zone 7 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01640 | Zone 7 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01641 | Zone 7 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01642 | Zone 7 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01643 | Zone 7 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01644 | Zone 7 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01645 | Zone 7 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01646 | Zone 7 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01647 | Zone 7 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01648 | Zone 7 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01649 | Zone 7 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01650 | Zone 7 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01651 | Zone 7 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01652 | Zone 7 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01653 | Zone 7 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01654 | Zone 7 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01655 | Zone 7 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01656 | Zone 7 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01657 | Zone 7 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01701 | Zone 8 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01702 | Zone 8 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01703 | Zone 8 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01704 | Zone 8 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01705 | Zone 8 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01706 | Zone 8 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01707 | Zone 8 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01708 | Zone 8 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01709 | Zone 8 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01710 | Zone 8 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01711 | Zone 8 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01712 | Zone 8 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01713 | Zone 8 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01714 | Zone 8 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01715 | Zone 8 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01716 | Zone 8 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01717 | Zone 8 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01718 | Zone 8 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01719 | Zone 8 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01720 | Zone 8 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01721 | Zone 8 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01722 | Zone 8 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01723 | Zone 8 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01724 | Zone 8 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01725 | Zone 8 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01726 | Zone 8 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01727 | Zone 8 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01728 | Zone 8 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01729 | Zone 8 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01730 | Zone 8 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01731 | Zone 8 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01732 | Zone 8 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01733 | Zone 8 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01734 | Zone 8 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01735 | Zone 8 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01736 | Zone 8 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01737 | Zone 8 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01738 | Zone 8 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01739 | Zone 8 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01740 | Zone 8 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01741 | Zone 8 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01742 | Zone 8 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01743 | Zone 8 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01744 | Zone 8 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01745 | Zone 8 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01746 | Zone 8 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01747 | Zone 8 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01748 | Zone 8 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01749 | Zone 8 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01750 | Zone 8 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01751 | Zone 8 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01752 | Zone 8 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01753 | Zone 8 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01754 | Zone 8 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01755 | Zone 8 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01756 | Zone 8 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01757 | Zone 8 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01801 | Zone 9 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01802 | Zone 9 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01803 | Zone 9 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01804 | Zone 9 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01805 | Zone 9 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01806 | Zone 9 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01807 | Zone 9 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01808 | Zone 9 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01809 | Zone 9 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01810 | Zone 9 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01811 | Zone 9 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01812 | Zone 9 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01813 | Zone 9 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01814 | Zone 9 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01815 | Zone 9 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01816 | Zone 9 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01817 | Zone 9 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01818 | Zone 9 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01819 | Zone 9 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01820 | Zone 9 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01821 | Zone 9 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01822 | Zone 9 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01823 | Zone 9 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01824 | Zone 9 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01825 | Zone 9 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01826 | Zone 9 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01827 | Zone 9 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01828 | Zone 9 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01829 | Zone 9 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01830 | Zone 9 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01831 | Zone 9 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01832 | Zone 9 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01833 | Zone 9 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01834 | Zone 9 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01835 | Zone 9 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01836 | Zone 9 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01837 | Zone 9 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01838 | Zone 9 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01839 | Zone 9 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01840 | Zone 9 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01841 | Zone 9 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01842 | Zone 9 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01843 | Zone 9 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01844 | Zone 9 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01845 | Zone 9 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01846 | Zone 9 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01847 | Zone 9 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01848 | Zone 9 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01849 | Zone 9 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01850 | Zone 9 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01851 | Zone 9 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01852 | Zone 9 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01853 | Zone 9 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01854 | Zone 9 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01855 | Zone 9 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01856 | Zone 9 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01857 | Zone 9 | Day 7 Event 3 End Time | 0 | 1440 | min
4:01901 | Zone 10 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:01902 | Zone 10 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:01903 | Zone 10 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:01904 | Zone 10 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01905 | Zone 10 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:01906 | Zone 10 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:01907 | Zone 10 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:01908 | Zone 10 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:01909 | Zone 10 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:01910 | Zone 10 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:01911 | Zone 10 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:01912 | Zone 10 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:01913 | Zone 10 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:01914 | Zone 10 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:01915 | Zone 10 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:01916 | Zone 10 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:01917 | Zone 10 | Day 1 Event 1 End Time | 0 | 1440 | min
4:01918 | Zone 10 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:01919 | Zone 10 | Day 1 Event 2 End Time | 0 | 1440 | min
4:01920 | Zone 10 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:01921 | Zone 10 | Day 1 Event 3 End Time | 0 | 1440 | min
4:01922 | Zone 10 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:01923 | Zone 10 | Day 2 Event 1 End Time | 0 | 1440 | min
4:01924 | Zone 10 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:01925 | Zone 10 | Day 2 Event 2 End Time | 0 | 1440 | min
4:01926 | Zone 10 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:01927 | Zone 10 | Day 2 Event 3 End Time | 0 | 1440 | min
4:01928 | Zone 10 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:01929 | Zone 10 | Day 3 Event 1 End Time | 0 | 1440 | min
4:01930 | Zone 10 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:01931 | Zone 10 | Day 3 Event 2 End Time | 0 | 1440 | min
4:01932 | Zone 10 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:01933 | Zone 10 | Day 3 Event 3 End Time | 0 | 1440 | min
4:01934 | Zone 10 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:01935 | Zone 10 | Day 4 Event 1 End Time | 0 | 1440 | min
4:01936 | Zone 10 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:01937 | Zone 10 | Day 4 Event 2 End Time | 0 | 1440 | min
4:01938 | Zone 10 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:01939 | Zone 10 | Day 4 Event 3 End Time | 0 | 1440 | min
4:01940 | Zone 10 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:01941 | Zone 10 | Day 5 Event 1 End Time | 0 | 1440 | min
4:01942 | Zone 10 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:01943 | Zone 10 | Day 5 Event 2 End Time | 0 | 1440 | min
4:01944 | Zone 10 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:01945 | Zone 10 | Day 5 Event 3 End Time | 0 | 1440 | min
4:01946 | Zone 10 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:01947 | Zone 10 | Day 6 Event 1 End Time | 0 | 1440 | min
4:01948 | Zone 10 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:01949 | Zone 10 | Day 6 Event 2 End Time | 0 | 1440 | min
4:01950 | Zone 10 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:01951 | Zone 10 | Day 6 Event 3 End Time | 0 | 1440 | min
4:01952 | Zone 10 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:01953 | Zone 10 | Day 7 Event 1 End Time | 0 | 1440 | min
4:01954 | Zone 10 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:01955 | Zone 10 | Day 7 Event 2 End Time | 0 | 1440 | min
4:01956 | Zone 10 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:01957 | Zone 10 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02001 | Zone 11 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02002 | Zone 11 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02003 | Zone 11 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02004 | Zone 11 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02005 | Zone 11 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02006 | Zone 11 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02007 | Zone 11 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02008 | Zone 11 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02009 | Zone 11 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02010 | Zone 11 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02011 | Zone 11 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02012 | Zone 11 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02013 | Zone 11 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02014 | Zone 11 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02015 | Zone 11 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02016 | Zone 11 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02017 | Zone 11 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02018 | Zone 11 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02019 | Zone 11 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02020 | Zone 11 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02021 | Zone 11 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02022 | Zone 11 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02023 | Zone 11 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02024 | Zone 11 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02025 | Zone 11 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02026 | Zone 11 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02027 | Zone 11 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02028 | Zone 11 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02029 | Zone 11 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02030 | Zone 11 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02031 | Zone 11 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02032 | Zone 11 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02033 | Zone 11 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02034 | Zone 11 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02035 | Zone 11 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02036 | Zone 11 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02037 | Zone 11 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02038 | Zone 11 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02039 | Zone 11 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02040 | Zone 11 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02041 | Zone 11 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02042 | Zone 11 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02043 | Zone 11 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02044 | Zone 11 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02045 | Zone 11 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02046 | Zone 11 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02047 | Zone 11 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02048 | Zone 11 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02049 | Zone 11 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02050 | Zone 11 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02051 | Zone 11 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02052 | Zone 11 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02053 | Zone 11 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02054 | Zone 11 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02055 | Zone 11 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02056 | Zone 11 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02057 | Zone 11 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02101 | Zone 12 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02102 | Zone 12 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02103 | Zone 12 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02104 | Zone 12 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02105 | Zone 12 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02106 | Zone 12 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02107 | Zone 12 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02108 | Zone 12 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02109 | Zone 12 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02110 | Zone 12 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02111 | Zone 12 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02112 | Zone 12 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02113 | Zone 12 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02114 | Zone 12 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02115 | Zone 12 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02116 | Zone 12 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02117 | Zone 12 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02118 | Zone 12 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02119 | Zone 12 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02120 | Zone 12 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02121 | Zone 12 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02122 | Zone 12 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02123 | Zone 12 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02124 | Zone 12 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02125 | Zone 12 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02126 | Zone 12 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02127 | Zone 12 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02128 | Zone 12 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02129 | Zone 12 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02130 | Zone 12 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02131 | Zone 12 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02132 | Zone 12 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02133 | Zone 12 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02134 | Zone 12 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02135 | Zone 12 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02136 | Zone 12 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02137 | Zone 12 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02138 | Zone 12 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02139 | Zone 12 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02140 | Zone 12 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02141 | Zone 12 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02142 | Zone 12 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02143 | Zone 12 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02144 | Zone 12 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02145 | Zone 12 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02146 | Zone 12 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02147 | Zone 12 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02148 | Zone 12 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02149 | Zone 12 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02150 | Zone 12 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02151 | Zone 12 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02152 | Zone 12 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02153 | Zone 12 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02154 | Zone 12 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02155 | Zone 12 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02156 | Zone 12 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02157 | Zone 12 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02201 | Zone 13 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02202 | Zone 13 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02203 | Zone 13 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02204 | Zone 13 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02205 | Zone 13 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02206 | Zone 13 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02207 | Zone 13 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02208 | Zone 13 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02209 | Zone 13 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02210 | Zone 13 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02211 | Zone 13 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02212 | Zone 13 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02213 | Zone 13 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02214 | Zone 13 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02215 | Zone 13 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02216 | Zone 13 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02217 | Zone 13 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02218 | Zone 13 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02219 | Zone 13 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02220 | Zone 13 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02221 | Zone 13 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02222 | Zone 13 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02223 | Zone 13 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02224 | Zone 13 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02225 | Zone 13 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02226 | Zone 13 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02227 | Zone 13 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02228 | Zone 13 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02229 | Zone 13 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02230 | Zone 13 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02231 | Zone 13 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02232 | Zone 13 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02233 | Zone 13 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02234 | Zone 13 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02235 | Zone 13 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02236 | Zone 13 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02237 | Zone 13 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02238 | Zone 13 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02239 | Zone 13 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02240 | Zone 13 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02241 | Zone 13 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02242 | Zone 13 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02243 | Zone 13 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02244 | Zone 13 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02245 | Zone 13 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02246 | Zone 13 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02247 | Zone 13 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02248 | Zone 13 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02249 | Zone 13 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02250 | Zone 13 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02251 | Zone 13 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02252 | Zone 13 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02253 | Zone 13 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02254 | Zone 13 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02255 | Zone 13 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02256 | Zone 13 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02257 | Zone 13 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02301 | Zone 14 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02302 | Zone 14 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02303 | Zone 14 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02304 | Zone 14 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02305 | Zone 14 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02306 | Zone 14 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02307 | Zone 14 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02308 | Zone 14 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02309 | Zone 14 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02310 | Zone 14 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02311 | Zone 14 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02312 | Zone 14 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02313 | Zone 14 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02314 | Zone 14 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02315 | Zone 14 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02316 | Zone 14 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02317 | Zone 14 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02318 | Zone 14 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02319 | Zone 14 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02320 | Zone 14 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02321 | Zone 14 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02322 | Zone 14 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02323 | Zone 14 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02324 | Zone 14 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02325 | Zone 14 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02326 | Zone 14 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02327 | Zone 14 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02328 | Zone 14 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02329 | Zone 14 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02330 | Zone 14 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02331 | Zone 14 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02332 | Zone 14 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02333 | Zone 14 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02334 | Zone 14 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02335 | Zone 14 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02336 | Zone 14 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02337 | Zone 14 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02338 | Zone 14 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02339 | Zone 14 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02340 | Zone 14 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02341 | Zone 14 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02342 | Zone 14 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02343 | Zone 14 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02344 | Zone 14 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02345 | Zone 14 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02346 | Zone 14 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02347 | Zone 14 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02348 | Zone 14 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02349 | Zone 14 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02350 | Zone 14 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02351 | Zone 14 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02352 | Zone 14 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02353 | Zone 14 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02354 | Zone 14 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02355 | Zone 14 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02356 | Zone 14 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02357 | Zone 14 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02401 | Zone 15 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02402 | Zone 15 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02403 | Zone 15 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02404 | Zone 15 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02405 | Zone 15 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02406 | Zone 15 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02407 | Zone 15 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02408 | Zone 15 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02409 | Zone 15 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02410 | Zone 15 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02411 | Zone 15 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02412 | Zone 15 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02413 | Zone 15 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02414 | Zone 15 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02415 | Zone 15 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02416 | Zone 15 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02417 | Zone 15 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02418 | Zone 15 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02419 | Zone 15 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02420 | Zone 15 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02421 | Zone 15 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02422 | Zone 15 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02423 | Zone 15 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02424 | Zone 15 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02425 | Zone 15 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02426 | Zone 15 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02427 | Zone 15 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02428 | Zone 15 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02429 | Zone 15 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02430 | Zone 15 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02431 | Zone 15 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02432 | Zone 15 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02433 | Zone 15 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02434 | Zone 15 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02435 | Zone 15 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02436 | Zone 15 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02437 | Zone 15 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02438 | Zone 15 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02439 | Zone 15 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02440 | Zone 15 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02441 | Zone 15 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02442 | Zone 15 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02443 | Zone 15 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02444 | Zone 15 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02445 | Zone 15 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02446 | Zone 15 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02447 | Zone 15 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02448 | Zone 15 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02449 | Zone 15 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02450 | Zone 15 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02451 | Zone 15 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02452 | Zone 15 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02453 | Zone 15 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02454 | Zone 15 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02455 | Zone 15 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02456 | Zone 15 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02457 | Zone 15 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02501 | Zone 16 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02502 | Zone 16 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02503 | Zone 16 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02504 | Zone 16 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02505 | Zone 16 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02506 | Zone 16 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02507 | Zone 16 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02508 | Zone 16 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02509 | Zone 16 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02510 | Zone 16 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02511 | Zone 16 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02512 | Zone 16 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02513 | Zone 16 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02514 | Zone 16 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02515 | Zone 16 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02516 | Zone 16 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02517 | Zone 16 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02518 | Zone 16 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02519 | Zone 16 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02520 | Zone 16 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02521 | Zone 16 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02522 | Zone 16 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02523 | Zone 16 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02524 | Zone 16 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02525 | Zone 16 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02526 | Zone 16 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02527 | Zone 16 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02528 | Zone 16 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02529 | Zone 16 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02530 | Zone 16 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02531 | Zone 16 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02532 | Zone 16 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02533 | Zone 16 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02534 | Zone 16 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02535 | Zone 16 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02536 | Zone 16 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02537 | Zone 16 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02538 | Zone 16 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02539 | Zone 16 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02540 | Zone 16 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02541 | Zone 16 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02542 | Zone 16 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02543 | Zone 16 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02544 | Zone 16 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02545 | Zone 16 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02546 | Zone 16 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02547 | Zone 16 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02548 | Zone 16 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02549 | Zone 16 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02550 | Zone 16 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02551 | Zone 16 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02552 | Zone 16 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02553 | Zone 16 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02554 | Zone 16 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02555 | Zone 16 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02556 | Zone 16 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02557 | Zone 16 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02601 | Zone 17 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02602 | Zone 17 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02603 | Zone 17 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02604 | Zone 17 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02605 | Zone 17 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02606 | Zone 17 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02607 | Zone 17 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02608 | Zone 17 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02609 | Zone 17 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02610 | Zone 17 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02611 | Zone 17 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02612 | Zone 17 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02613 | Zone 17 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02614 | Zone 17 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02615 | Zone 17 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02616 | Zone 17 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02617 | Zone 17 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02618 | Zone 17 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02619 | Zone 17 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02620 | Zone 17 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02621 | Zone 17 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02622 | Zone 17 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02623 | Zone 17 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02624 | Zone 17 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02625 | Zone 17 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02626 | Zone 17 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02627 | Zone 17 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02628 | Zone 17 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02629 | Zone 17 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02630 | Zone 17 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02631 | Zone 17 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02632 | Zone 17 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02633 | Zone 17 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02634 | Zone 17 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02635 | Zone 17 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02636 | Zone 17 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02637 | Zone 17 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02638 | Zone 17 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02639 | Zone 17 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02640 | Zone 17 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02641 | Zone 17 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02642 | Zone 17 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02643 | Zone 17 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02644 | Zone 17 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02645 | Zone 17 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02646 | Zone 17 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02647 | Zone 17 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02648 | Zone 17 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02649 | Zone 17 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02650 | Zone 17 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02651 | Zone 17 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02652 | Zone 17 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02653 | Zone 17 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02654 | Zone 17 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02655 | Zone 17 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02656 | Zone 17 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02657 | Zone 17 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02701 | Zone 18 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02702 | Zone 18 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02703 | Zone 18 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02704 | Zone 18 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02705 | Zone 18 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02706 | Zone 18 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02707 | Zone 18 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02708 | Zone 18 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02709 | Zone 18 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02710 | Zone 18 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02711 | Zone 18 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02712 | Zone 18 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02713 | Zone 18 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02714 | Zone 18 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02715 | Zone 18 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02716 | Zone 18 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02717 | Zone 18 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02718 | Zone 18 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02719 | Zone 18 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02720 | Zone 18 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02721 | Zone 18 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02722 | Zone 18 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02723 | Zone 18 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02724 | Zone 18 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02725 | Zone 18 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02726 | Zone 18 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02727 | Zone 18 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02728 | Zone 18 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02729 | Zone 18 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02730 | Zone 18 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02731 | Zone 18 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02732 | Zone 18 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02733 | Zone 18 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02734 | Zone 18 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02735 | Zone 18 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02736 | Zone 18 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02737 | Zone 18 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02738 | Zone 18 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02739 | Zone 18 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02740 | Zone 18 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02741 | Zone 18 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02742 | Zone 18 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02743 | Zone 18 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02744 | Zone 18 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02745 | Zone 18 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02746 | Zone 18 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02747 | Zone 18 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02748 | Zone 18 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02749 | Zone 18 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02750 | Zone 18 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02751 | Zone 18 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02752 | Zone 18 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02753 | Zone 18 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02754 | Zone 18 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02755 | Zone 18 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02756 | Zone 18 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02757 | Zone 18 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02801 | Zone 19 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02802 | Zone 19 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02803 | Zone 19 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02804 | Zone 19 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02805 | Zone 19 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02806 | Zone 19 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02807 | Zone 19 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02808 | Zone 19 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02809 | Zone 19 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02810 | Zone 19 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02811 | Zone 19 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02812 | Zone 19 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02813 | Zone 19 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02814 | Zone 19 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02815 | Zone 19 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02816 | Zone 19 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02817 | Zone 19 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02818 | Zone 19 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02819 | Zone 19 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02820 | Zone 19 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02821 | Zone 19 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02822 | Zone 19 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02823 | Zone 19 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02824 | Zone 19 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02825 | Zone 19 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02826 | Zone 19 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02827 | Zone 19 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02828 | Zone 19 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02829 | Zone 19 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02830 | Zone 19 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02831 | Zone 19 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02832 | Zone 19 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02833 | Zone 19 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02834 | Zone 19 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02835 | Zone 19 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02836 | Zone 19 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02837 | Zone 19 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02838 | Zone 19 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02839 | Zone 19 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02840 | Zone 19 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02841 | Zone 19 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02842 | Zone 19 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02843 | Zone 19 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02844 | Zone 19 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02845 | Zone 19 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02846 | Zone 19 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02847 | Zone 19 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02848 | Zone 19 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02849 | Zone 19 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02850 | Zone 19 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02851 | Zone 19 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02852 | Zone 19 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02853 | Zone 19 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02854 | Zone 19 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02855 | Zone 19 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02856 | Zone 19 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02857 | Zone 19 | Day 7 Event 3 End Time | 0 | 1440 | min
4:02901 | Zone 20 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:02902 | Zone 20 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:02903 | Zone 20 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:02904 | Zone 20 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02905 | Zone 20 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:02906 | Zone 20 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:02907 | Zone 20 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:02908 | Zone 20 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:02909 | Zone 20 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:02910 | Zone 20 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:02911 | Zone 20 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:02912 | Zone 20 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:02913 | Zone 20 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:02914 | Zone 20 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:02915 | Zone 20 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:02916 | Zone 20 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:02917 | Zone 20 | Day 1 Event 1 End Time | 0 | 1440 | min
4:02918 | Zone 20 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:02919 | Zone 20 | Day 1 Event 2 End Time | 0 | 1440 | min
4:02920 | Zone 20 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:02921 | Zone 20 | Day 1 Event 3 End Time | 0 | 1440 | min
4:02922 | Zone 20 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:02923 | Zone 20 | Day 2 Event 1 End Time | 0 | 1440 | min
4:02924 | Zone 20 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:02925 | Zone 20 | Day 2 Event 2 End Time | 0 | 1440 | min
4:02926 | Zone 20 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:02927 | Zone 20 | Day 2 Event 3 End Time | 0 | 1440 | min
4:02928 | Zone 20 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:02929 | Zone 20 | Day 3 Event 1 End Time | 0 | 1440 | min
4:02930 | Zone 20 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:02931 | Zone 20 | Day 3 Event 2 End Time | 0 | 1440 | min
4:02932 | Zone 20 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:02933 | Zone 20 | Day 3 Event 3 End Time | 0 | 1440 | min
4:02934 | Zone 20 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:02935 | Zone 20 | Day 4 Event 1 End Time | 0 | 1440 | min
4:02936 | Zone 20 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:02937 | Zone 20 | Day 4 Event 2 End Time | 0 | 1440 | min
4:02938 | Zone 20 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:02939 | Zone 20 | Day 4 Event 3 End Time | 0 | 1440 | min
4:02940 | Zone 20 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:02941 | Zone 20 | Day 5 Event 1 End Time | 0 | 1440 | min
4:02942 | Zone 20 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:02943 | Zone 20 | Day 5 Event 2 End Time | 0 | 1440 | min
4:02944 | Zone 20 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:02945 | Zone 20 | Day 5 Event 3 End Time | 0 | 1440 | min
4:02946 | Zone 20 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:02947 | Zone 20 | Day 6 Event 1 End Time | 0 | 1440 | min
4:02948 | Zone 20 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:02949 | Zone 20 | Day 6 Event 2 End Time | 0 | 1440 | min
4:02950 | Zone 20 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:02951 | Zone 20 | Day 6 Event 3 End Time | 0 | 1440 | min
4:02952 | Zone 20 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:02953 | Zone 20 | Day 7 Event 1 End Time | 0 | 1440 | min
4:02954 | Zone 20 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:02955 | Zone 20 | Day 7 Event 2 End Time | 0 | 1440 | min
4:02956 | Zone 20 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:02957 | Zone 20 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03001 | Zone 21 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03002 | Zone 21 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03003 | Zone 21 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03004 | Zone 21 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03005 | Zone 21 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03006 | Zone 21 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03007 | Zone 21 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03008 | Zone 21 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03009 | Zone 21 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03010 | Zone 21 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03011 | Zone 21 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03012 | Zone 21 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03013 | Zone 21 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03014 | Zone 21 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03015 | Zone 21 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03016 | Zone 21 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03017 | Zone 21 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03018 | Zone 21 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03019 | Zone 21 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03020 | Zone 21 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03021 | Zone 21 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03022 | Zone 21 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03023 | Zone 21 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03024 | Zone 21 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03025 | Zone 21 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03026 | Zone 21 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03027 | Zone 21 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03028 | Zone 21 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03029 | Zone 21 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03030 | Zone 21 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03031 | Zone 21 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03032 | Zone 21 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03033 | Zone 21 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03034 | Zone 21 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03035 | Zone 21 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03036 | Zone 21 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03037 | Zone 21 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03038 | Zone 21 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03039 | Zone 21 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03040 | Zone 21 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03041 | Zone 21 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03042 | Zone 21 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03043 | Zone 21 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03044 | Zone 21 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03045 | Zone 21 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03046 | Zone 21 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03047 | Zone 21 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03048 | Zone 21 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03049 | Zone 21 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03050 | Zone 21 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03051 | Zone 21 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03052 | Zone 21 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03053 | Zone 21 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03054 | Zone 21 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03055 | Zone 21 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03056 | Zone 21 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03057 | Zone 21 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03101 | Zone 22 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03102 | Zone 22 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03103 | Zone 22 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03104 | Zone 22 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03105 | Zone 22 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03106 | Zone 22 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03107 | Zone 22 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03108 | Zone 22 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03109 | Zone 22 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03110 | Zone 22 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03111 | Zone 22 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03112 | Zone 22 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03113 | Zone 22 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03114 | Zone 22 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03115 | Zone 22 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03116 | Zone 22 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03117 | Zone 22 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03118 | Zone 22 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03119 | Zone 22 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03120 | Zone 22 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03121 | Zone 22 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03122 | Zone 22 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03123 | Zone 22 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03124 | Zone 22 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03125 | Zone 22 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03126 | Zone 22 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03127 | Zone 22 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03128 | Zone 22 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03129 | Zone 22 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03130 | Zone 22 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03131 | Zone 22 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03132 | Zone 22 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03133 | Zone 22 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03134 | Zone 22 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03135 | Zone 22 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03136 | Zone 22 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03137 | Zone 22 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03138 | Zone 22 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03139 | Zone 22 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03140 | Zone 22 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03141 | Zone 22 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03142 | Zone 22 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03143 | Zone 22 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03144 | Zone 22 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03145 | Zone 22 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03146 | Zone 22 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03147 | Zone 22 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03148 | Zone 22 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03149 | Zone 22 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03150 | Zone 22 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03151 | Zone 22 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03152 | Zone 22 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03153 | Zone 22 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03154 | Zone 22 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03155 | Zone 22 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03156 | Zone 22 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03157 | Zone 22 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03201 | Zone 23 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03202 | Zone 23 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03203 | Zone 23 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03204 | Zone 23 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03205 | Zone 23 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03206 | Zone 23 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03207 | Zone 23 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03208 | Zone 23 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03209 | Zone 23 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03210 | Zone 23 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03211 | Zone 23 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03212 | Zone 23 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03213 | Zone 23 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03214 | Zone 23 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03215 | Zone 23 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03216 | Zone 23 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03217 | Zone 23 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03218 | Zone 23 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03219 | Zone 23 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03220 | Zone 23 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03221 | Zone 23 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03222 | Zone 23 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03223 | Zone 23 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03224 | Zone 23 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03225 | Zone 23 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03226 | Zone 23 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03227 | Zone 23 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03228 | Zone 23 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03229 | Zone 23 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03230 | Zone 23 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03231 | Zone 23 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03232 | Zone 23 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03233 | Zone 23 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03234 | Zone 23 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03235 | Zone 23 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03236 | Zone 23 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03237 | Zone 23 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03238 | Zone 23 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03239 | Zone 23 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03240 | Zone 23 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03241 | Zone 23 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03242 | Zone 23 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03243 | Zone 23 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03244 | Zone 23 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03245 | Zone 23 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03246 | Zone 23 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03247 | Zone 23 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03248 | Zone 23 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03249 | Zone 23 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03250 | Zone 23 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03251 | Zone 23 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03252 | Zone 23 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03253 | Zone 23 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03254 | Zone 23 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03255 | Zone 23 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03256 | Zone 23 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03257 | Zone 23 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03301 | Zone 24 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03302 | Zone 24 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03303 | Zone 24 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03304 | Zone 24 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03305 | Zone 24 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03306 | Zone 24 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03307 | Zone 24 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03308 | Zone 24 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03309 | Zone 24 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03310 | Zone 24 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03311 | Zone 24 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03312 | Zone 24 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03313 | Zone 24 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03314 | Zone 24 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03315 | Zone 24 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03316 | Zone 24 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03317 | Zone 24 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03318 | Zone 24 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03319 | Zone 24 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03320 | Zone 24 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03321 | Zone 24 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03322 | Zone 24 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03323 | Zone 24 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03324 | Zone 24 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03325 | Zone 24 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03326 | Zone 24 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03327 | Zone 24 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03328 | Zone 24 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03329 | Zone 24 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03330 | Zone 24 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03331 | Zone 24 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03332 | Zone 24 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03333 | Zone 24 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03334 | Zone 24 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03335 | Zone 24 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03336 | Zone 24 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03337 | Zone 24 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03338 | Zone 24 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03339 | Zone 24 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03340 | Zone 24 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03341 | Zone 24 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03342 | Zone 24 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03343 | Zone 24 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03344 | Zone 24 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03345 | Zone 24 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03346 | Zone 24 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03347 | Zone 24 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03348 | Zone 24 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03349 | Zone 24 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03350 | Zone 24 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03351 | Zone 24 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03352 | Zone 24 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03353 | Zone 24 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03354 | Zone 24 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03355 | Zone 24 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03356 | Zone 24 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03357 | Zone 24 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03401 | Zone 25 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03402 | Zone 25 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03403 | Zone 25 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03404 | Zone 25 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03405 | Zone 25 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03406 | Zone 25 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03407 | Zone 25 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03408 | Zone 25 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03409 | Zone 25 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03410 | Zone 25 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03411 | Zone 25 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03412 | Zone 25 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03413 | Zone 25 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03414 | Zone 25 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03415 | Zone 25 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03416 | Zone 25 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03417 | Zone 25 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03418 | Zone 25 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03419 | Zone 25 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03420 | Zone 25 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03421 | Zone 25 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03422 | Zone 25 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03423 | Zone 25 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03424 | Zone 25 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03425 | Zone 25 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03426 | Zone 25 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03427 | Zone 25 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03428 | Zone 25 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03429 | Zone 25 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03430 | Zone 25 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03431 | Zone 25 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03432 | Zone 25 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03433 | Zone 25 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03434 | Zone 25 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03435 | Zone 25 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03436 | Zone 25 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03437 | Zone 25 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03438 | Zone 25 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03439 | Zone 25 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03440 | Zone 25 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03441 | Zone 25 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03442 | Zone 25 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03443 | Zone 25 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03444 | Zone 25 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03445 | Zone 25 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03446 | Zone 25 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03447 | Zone 25 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03448 | Zone 25 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03449 | Zone 25 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03450 | Zone 25 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03451 | Zone 25 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03452 | Zone 25 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03453 | Zone 25 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03454 | Zone 25 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03455 | Zone 25 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03456 | Zone 25 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03457 | Zone 25 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03501 | Zone 26 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03502 | Zone 26 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03503 | Zone 26 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03504 | Zone 26 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03505 | Zone 26 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03506 | Zone 26 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03507 | Zone 26 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03508 | Zone 26 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03509 | Zone 26 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03510 | Zone 26 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03511 | Zone 26 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03512 | Zone 26 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03513 | Zone 26 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03514 | Zone 26 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03515 | Zone 26 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03516 | Zone 26 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03517 | Zone 26 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03518 | Zone 26 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03519 | Zone 26 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03520 | Zone 26 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03521 | Zone 26 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03522 | Zone 26 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03523 | Zone 26 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03524 | Zone 26 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03525 | Zone 26 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03526 | Zone 26 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03527 | Zone 26 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03528 | Zone 26 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03529 | Zone 26 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03530 | Zone 26 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03531 | Zone 26 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03532 | Zone 26 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03533 | Zone 26 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03534 | Zone 26 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03535 | Zone 26 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03536 | Zone 26 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03537 | Zone 26 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03538 | Zone 26 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03539 | Zone 26 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03540 | Zone 26 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03541 | Zone 26 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03542 | Zone 26 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03543 | Zone 26 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03544 | Zone 26 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03545 | Zone 26 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03546 | Zone 26 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03547 | Zone 26 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03548 | Zone 26 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03549 | Zone 26 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03550 | Zone 26 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03551 | Zone 26 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03552 | Zone 26 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03553 | Zone 26 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03554 | Zone 26 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03555 | Zone 26 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03556 | Zone 26 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03557 | Zone 26 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03601 | Zone 27 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03602 | Zone 27 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03603 | Zone 27 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03604 | Zone 27 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03605 | Zone 27 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03606 | Zone 27 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03607 | Zone 27 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03608 | Zone 27 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03609 | Zone 27 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03610 | Zone 27 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03611 | Zone 27 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03612 | Zone 27 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03613 | Zone 27 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03614 | Zone 27 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03615 | Zone 27 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03616 | Zone 27 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03617 | Zone 27 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03618 | Zone 27 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03619 | Zone 27 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03620 | Zone 27 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03621 | Zone 27 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03622 | Zone 27 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03623 | Zone 27 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03624 | Zone 27 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03625 | Zone 27 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03626 | Zone 27 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03627 | Zone 27 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03628 | Zone 27 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03629 | Zone 27 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03630 | Zone 27 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03631 | Zone 27 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03632 | Zone 27 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03633 | Zone 27 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03634 | Zone 27 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03635 | Zone 27 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03636 | Zone 27 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03637 | Zone 27 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03638 | Zone 27 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03639 | Zone 27 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03640 | Zone 27 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03641 | Zone 27 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03642 | Zone 27 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03643 | Zone 27 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03644 | Zone 27 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03645 | Zone 27 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03646 | Zone 27 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03647 | Zone 27 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03648 | Zone 27 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03649 | Zone 27 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03650 | Zone 27 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03651 | Zone 27 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03652 | Zone 27 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03653 | Zone 27 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03654 | Zone 27 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03655 | Zone 27 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03656 | Zone 27 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03657 | Zone 27 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03701 | Zone 28 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03702 | Zone 28 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03703 | Zone 28 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03704 | Zone 28 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03705 | Zone 28 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03706 | Zone 28 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03707 | Zone 28 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03708 | Zone 28 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03709 | Zone 28 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03710 | Zone 28 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03711 | Zone 28 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03712 | Zone 28 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03713 | Zone 28 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03714 | Zone 28 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03715 | Zone 28 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03716 | Zone 28 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03717 | Zone 28 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03718 | Zone 28 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03719 | Zone 28 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03720 | Zone 28 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03721 | Zone 28 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03722 | Zone 28 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03723 | Zone 28 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03724 | Zone 28 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03725 | Zone 28 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03726 | Zone 28 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03727 | Zone 28 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03728 | Zone 28 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03729 | Zone 28 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03730 | Zone 28 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03731 | Zone 28 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03732 | Zone 28 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03733 | Zone 28 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03734 | Zone 28 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03735 | Zone 28 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03736 | Zone 28 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03737 | Zone 28 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03738 | Zone 28 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03739 | Zone 28 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03740 | Zone 28 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03741 | Zone 28 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03742 | Zone 28 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03743 | Zone 28 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03744 | Zone 28 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03745 | Zone 28 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03746 | Zone 28 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03747 | Zone 28 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03748 | Zone 28 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03749 | Zone 28 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03750 | Zone 28 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03751 | Zone 28 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03752 | Zone 28 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03753 | Zone 28 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03754 | Zone 28 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03755 | Zone 28 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03756 | Zone 28 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03757 | Zone 28 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03801 | Zone 29 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03802 | Zone 29 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03803 | Zone 29 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03804 | Zone 29 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03805 | Zone 29 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03806 | Zone 29 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03807 | Zone 29 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03808 | Zone 29 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03809 | Zone 29 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03810 | Zone 29 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03811 | Zone 29 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03812 | Zone 29 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03813 | Zone 29 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03814 | Zone 29 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03815 | Zone 29 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03816 | Zone 29 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03817 | Zone 29 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03818 | Zone 29 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03819 | Zone 29 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03820 | Zone 29 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03821 | Zone 29 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03822 | Zone 29 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03823 | Zone 29 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03824 | Zone 29 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03825 | Zone 29 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03826 | Zone 29 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03827 | Zone 29 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03828 | Zone 29 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03829 | Zone 29 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03830 | Zone 29 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03831 | Zone 29 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03832 | Zone 29 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03833 | Zone 29 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03834 | Zone 29 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03835 | Zone 29 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03836 | Zone 29 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03837 | Zone 29 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03838 | Zone 29 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03839 | Zone 29 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03840 | Zone 29 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03841 | Zone 29 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03842 | Zone 29 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03843 | Zone 29 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03844 | Zone 29 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03845 | Zone 29 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03846 | Zone 29 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03847 | Zone 29 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03848 | Zone 29 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03849 | Zone 29 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03850 | Zone 29 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03851 | Zone 29 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03852 | Zone 29 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03853 | Zone 29 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03854 | Zone 29 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03855 | Zone 29 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03856 | Zone 29 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03857 | Zone 29 | Day 7 Event 3 End Time | 0 | 1440 | min
4:03901 | Zone 30 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:03902 | Zone 30 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:03903 | Zone 30 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:03904 | Zone 30 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03905 | Zone 30 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:03906 | Zone 30 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:03907 | Zone 30 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:03908 | Zone 30 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:03909 | Zone 30 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:03910 | Zone 30 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:03911 | Zone 30 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:03912 | Zone 30 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:03913 | Zone 30 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:03914 | Zone 30 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:03915 | Zone 30 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:03916 | Zone 30 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:03917 | Zone 30 | Day 1 Event 1 End Time | 0 | 1440 | min
4:03918 | Zone 30 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:03919 | Zone 30 | Day 1 Event 2 End Time | 0 | 1440 | min
4:03920 | Zone 30 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:03921 | Zone 30 | Day 1 Event 3 End Time | 0 | 1440 | min
4:03922 | Zone 30 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:03923 | Zone 30 | Day 2 Event 1 End Time | 0 | 1440 | min
4:03924 | Zone 30 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:03925 | Zone 30 | Day 2 Event 2 End Time | 0 | 1440 | min
4:03926 | Zone 30 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:03927 | Zone 30 | Day 2 Event 3 End Time | 0 | 1440 | min
4:03928 | Zone 30 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:03929 | Zone 30 | Day 3 Event 1 End Time | 0 | 1440 | min
4:03930 | Zone 30 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:03931 | Zone 30 | Day 3 Event 2 End Time | 0 | 1440 | min
4:03932 | Zone 30 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:03933 | Zone 30 | Day 3 Event 3 End Time | 0 | 1440 | min
4:03934 | Zone 30 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:03935 | Zone 30 | Day 4 Event 1 End Time | 0 | 1440 | min
4:03936 | Zone 30 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:03937 | Zone 30 | Day 4 Event 2 End Time | 0 | 1440 | min
4:03938 | Zone 30 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:03939 | Zone 30 | Day 4 Event 3 End Time | 0 | 1440 | min
4:03940 | Zone 30 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:03941 | Zone 30 | Day 5 Event 1 End Time | 0 | 1440 | min
4:03942 | Zone 30 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:03943 | Zone 30 | Day 5 Event 2 End Time | 0 | 1440 | min
4:03944 | Zone 30 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:03945 | Zone 30 | Day 5 Event 3 End Time | 0 | 1440 | min
4:03946 | Zone 30 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:03947 | Zone 30 | Day 6 Event 1 End Time | 0 | 1440 | min
4:03948 | Zone 30 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:03949 | Zone 30 | Day 6 Event 2 End Time | 0 | 1440 | min
4:03950 | Zone 30 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:03951 | Zone 30 | Day 6 Event 3 End Time | 0 | 1440 | min
4:03952 | Zone 30 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:03953 | Zone 30 | Day 7 Event 1 End Time | 0 | 1440 | min
4:03954 | Zone 30 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:03955 | Zone 30 | Day 7 Event 2 End Time | 0 | 1440 | min
4:03956 | Zone 30 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:03957 | Zone 30 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04001 | Zone 31 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04002 | Zone 31 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04003 | Zone 31 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04004 | Zone 31 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04005 | Zone 31 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04006 | Zone 31 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04007 | Zone 31 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04008 | Zone 31 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04009 | Zone 31 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04010 | Zone 31 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04011 | Zone 31 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04012 | Zone 31 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04013 | Zone 31 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04014 | Zone 31 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04015 | Zone 31 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04016 | Zone 31 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04017 | Zone 31 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04018 | Zone 31 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04019 | Zone 31 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04020 | Zone 31 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04021 | Zone 31 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04022 | Zone 31 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04023 | Zone 31 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04024 | Zone 31 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04025 | Zone 31 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04026 | Zone 31 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04027 | Zone 31 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04028 | Zone 31 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04029 | Zone 31 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04030 | Zone 31 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04031 | Zone 31 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04032 | Zone 31 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04033 | Zone 31 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04034 | Zone 31 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04035 | Zone 31 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04036 | Zone 31 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04037 | Zone 31 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04038 | Zone 31 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04039 | Zone 31 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04040 | Zone 31 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04041 | Zone 31 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04042 | Zone 31 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04043 | Zone 31 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04044 | Zone 31 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04045 | Zone 31 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04046 | Zone 31 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04047 | Zone 31 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04048 | Zone 31 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04049 | Zone 31 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04050 | Zone 31 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04051 | Zone 31 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04052 | Zone 31 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04053 | Zone 31 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04054 | Zone 31 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04055 | Zone 31 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04056 | Zone 31 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04057 | Zone 31 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04101 | Zone 32 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04102 | Zone 32 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04103 | Zone 32 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04104 | Zone 32 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04105 | Zone 32 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04106 | Zone 32 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04107 | Zone 32 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04108 | Zone 32 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04109 | Zone 32 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04110 | Zone 32 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04111 | Zone 32 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04112 | Zone 32 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04113 | Zone 32 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04114 | Zone 32 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04115 | Zone 32 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04116 | Zone 32 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04117 | Zone 32 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04118 | Zone 32 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04119 | Zone 32 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04120 | Zone 32 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04121 | Zone 32 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04122 | Zone 32 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04123 | Zone 32 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04124 | Zone 32 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04125 | Zone 32 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04126 | Zone 32 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04127 | Zone 32 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04128 | Zone 32 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04129 | Zone 32 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04130 | Zone 32 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04131 | Zone 32 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04132 | Zone 32 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04133 | Zone 32 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04134 | Zone 32 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04135 | Zone 32 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04136 | Zone 32 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04137 | Zone 32 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04138 | Zone 32 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04139 | Zone 32 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04140 | Zone 32 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04141 | Zone 32 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04142 | Zone 32 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04143 | Zone 32 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04144 | Zone 32 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04145 | Zone 32 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04146 | Zone 32 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04147 | Zone 32 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04148 | Zone 32 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04149 | Zone 32 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04150 | Zone 32 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04151 | Zone 32 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04152 | Zone 32 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04153 | Zone 32 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04154 | Zone 32 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04155 | Zone 32 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04156 | Zone 32 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04157 | Zone 32 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04201 | Zone 33 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04202 | Zone 33 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04203 | Zone 33 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04204 | Zone 33 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04205 | Zone 33 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04206 | Zone 33 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04207 | Zone 33 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04208 | Zone 33 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04209 | Zone 33 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04210 | Zone 33 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04211 | Zone 33 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04212 | Zone 33 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04213 | Zone 33 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04214 | Zone 33 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04215 | Zone 33 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04216 | Zone 33 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04217 | Zone 33 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04218 | Zone 33 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04219 | Zone 33 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04220 | Zone 33 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04221 | Zone 33 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04222 | Zone 33 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04223 | Zone 33 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04224 | Zone 33 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04225 | Zone 33 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04226 | Zone 33 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04227 | Zone 33 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04228 | Zone 33 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04229 | Zone 33 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04230 | Zone 33 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04231 | Zone 33 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04232 | Zone 33 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04233 | Zone 33 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04234 | Zone 33 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04235 | Zone 33 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04236 | Zone 33 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04237 | Zone 33 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04238 | Zone 33 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04239 | Zone 33 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04240 | Zone 33 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04241 | Zone 33 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04242 | Zone 33 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04243 | Zone 33 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04244 | Zone 33 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04245 | Zone 33 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04246 | Zone 33 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04247 | Zone 33 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04248 | Zone 33 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04249 | Zone 33 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04250 | Zone 33 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04251 | Zone 33 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04252 | Zone 33 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04253 | Zone 33 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04254 | Zone 33 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04255 | Zone 33 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04256 | Zone 33 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04257 | Zone 33 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04301 | Zone 34 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04302 | Zone 34 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04303 | Zone 34 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04304 | Zone 34 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04305 | Zone 34 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04306 | Zone 34 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04307 | Zone 34 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04308 | Zone 34 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04309 | Zone 34 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04310 | Zone 34 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04311 | Zone 34 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04312 | Zone 34 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04313 | Zone 34 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04314 | Zone 34 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04315 | Zone 34 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04316 | Zone 34 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04317 | Zone 34 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04318 | Zone 34 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04319 | Zone 34 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04320 | Zone 34 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04321 | Zone 34 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04322 | Zone 34 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04323 | Zone 34 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04324 | Zone 34 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04325 | Zone 34 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04326 | Zone 34 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04327 | Zone 34 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04328 | Zone 34 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04329 | Zone 34 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04330 | Zone 34 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04331 | Zone 34 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04332 | Zone 34 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04333 | Zone 34 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04334 | Zone 34 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04335 | Zone 34 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04336 | Zone 34 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04337 | Zone 34 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04338 | Zone 34 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04339 | Zone 34 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04340 | Zone 34 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04341 | Zone 34 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04342 | Zone 34 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04343 | Zone 34 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04344 | Zone 34 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04345 | Zone 34 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04346 | Zone 34 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04347 | Zone 34 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04348 | Zone 34 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04349 | Zone 34 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04350 | Zone 34 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04351 | Zone 34 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04352 | Zone 34 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04353 | Zone 34 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04354 | Zone 34 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04355 | Zone 34 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04356 | Zone 34 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04357 | Zone 34 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04401 | Zone 35 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04402 | Zone 35 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04403 | Zone 35 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04404 | Zone 35 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04405 | Zone 35 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04406 | Zone 35 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04407 | Zone 35 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04408 | Zone 35 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04409 | Zone 35 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04410 | Zone 35 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04411 | Zone 35 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04412 | Zone 35 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04413 | Zone 35 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04414 | Zone 35 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04415 | Zone 35 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04416 | Zone 35 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04417 | Zone 35 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04418 | Zone 35 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04419 | Zone 35 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04420 | Zone 35 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04421 | Zone 35 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04422 | Zone 35 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04423 | Zone 35 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04424 | Zone 35 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04425 | Zone 35 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04426 | Zone 35 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04427 | Zone 35 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04428 | Zone 35 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04429 | Zone 35 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04430 | Zone 35 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04431 | Zone 35 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04432 | Zone 35 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04433 | Zone 35 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04434 | Zone 35 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04435 | Zone 35 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04436 | Zone 35 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04437 | Zone 35 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04438 | Zone 35 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04439 | Zone 35 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04440 | Zone 35 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04441 | Zone 35 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04442 | Zone 35 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04443 | Zone 35 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04444 | Zone 35 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04445 | Zone 35 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04446 | Zone 35 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04447 | Zone 35 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04448 | Zone 35 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04449 | Zone 35 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04450 | Zone 35 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04451 | Zone 35 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04452 | Zone 35 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04453 | Zone 35 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04454 | Zone 35 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04455 | Zone 35 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04456 | Zone 35 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04457 | Zone 35 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04501 | Zone 36 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04502 | Zone 36 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04503 | Zone 36 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04504 | Zone 36 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04505 | Zone 36 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04506 | Zone 36 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04507 | Zone 36 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04508 | Zone 36 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04509 | Zone 36 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04510 | Zone 36 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04511 | Zone 36 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04512 | Zone 36 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04513 | Zone 36 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04514 | Zone 36 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04515 | Zone 36 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04516 | Zone 36 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04517 | Zone 36 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04518 | Zone 36 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04519 | Zone 36 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04520 | Zone 36 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04521 | Zone 36 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04522 | Zone 36 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04523 | Zone 36 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04524 | Zone 36 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04525 | Zone 36 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04526 | Zone 36 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04527 | Zone 36 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04528 | Zone 36 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04529 | Zone 36 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04530 | Zone 36 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04531 | Zone 36 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04532 | Zone 36 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04533 | Zone 36 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04534 | Zone 36 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04535 | Zone 36 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04536 | Zone 36 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04537 | Zone 36 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04538 | Zone 36 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04539 | Zone 36 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04540 | Zone 36 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04541 | Zone 36 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04542 | Zone 36 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04543 | Zone 36 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04544 | Zone 36 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04545 | Zone 36 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04546 | Zone 36 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04547 | Zone 36 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04548 | Zone 36 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04549 | Zone 36 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04550 | Zone 36 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04551 | Zone 36 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04552 | Zone 36 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04553 | Zone 36 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04554 | Zone 36 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04555 | Zone 36 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04556 | Zone 36 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04557 | Zone 36 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04601 | Zone 37 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04602 | Zone 37 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04603 | Zone 37 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04604 | Zone 37 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04605 | Zone 37 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04606 | Zone 37 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04607 | Zone 37 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04608 | Zone 37 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04609 | Zone 37 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04610 | Zone 37 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04611 | Zone 37 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04612 | Zone 37 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04613 | Zone 37 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04614 | Zone 37 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04615 | Zone 37 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04616 | Zone 37 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04617 | Zone 37 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04618 | Zone 37 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04619 | Zone 37 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04620 | Zone 37 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04621 | Zone 37 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04622 | Zone 37 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04623 | Zone 37 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04624 | Zone 37 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04625 | Zone 37 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04626 | Zone 37 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04627 | Zone 37 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04628 | Zone 37 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04629 | Zone 37 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04630 | Zone 37 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04631 | Zone 37 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04632 | Zone 37 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04633 | Zone 37 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04634 | Zone 37 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04635 | Zone 37 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04636 | Zone 37 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04637 | Zone 37 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04638 | Zone 37 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04639 | Zone 37 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04640 | Zone 37 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04641 | Zone 37 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04642 | Zone 37 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04643 | Zone 37 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04644 | Zone 37 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04645 | Zone 37 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04646 | Zone 37 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04647 | Zone 37 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04648 | Zone 37 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04649 | Zone 37 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04650 | Zone 37 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04651 | Zone 37 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04652 | Zone 37 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04653 | Zone 37 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04654 | Zone 37 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04655 | Zone 37 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04656 | Zone 37 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04657 | Zone 37 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04701 | Zone 38 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04702 | Zone 38 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04703 | Zone 38 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04704 | Zone 38 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04705 | Zone 38 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04706 | Zone 38 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04707 | Zone 38 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04708 | Zone 38 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04709 | Zone 38 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04710 | Zone 38 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04711 | Zone 38 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04712 | Zone 38 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04713 | Zone 38 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04714 | Zone 38 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04715 | Zone 38 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04716 | Zone 38 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04717 | Zone 38 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04718 | Zone 38 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04719 | Zone 38 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04720 | Zone 38 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04721 | Zone 38 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04722 | Zone 38 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04723 | Zone 38 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04724 | Zone 38 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04725 | Zone 38 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04726 | Zone 38 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04727 | Zone 38 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04728 | Zone 38 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04729 | Zone 38 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04730 | Zone 38 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04731 | Zone 38 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04732 | Zone 38 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04733 | Zone 38 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04734 | Zone 38 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04735 | Zone 38 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04736 | Zone 38 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04737 | Zone 38 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04738 | Zone 38 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04739 | Zone 38 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04740 | Zone 38 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04741 | Zone 38 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04742 | Zone 38 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04743 | Zone 38 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04744 | Zone 38 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04745 | Zone 38 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04746 | Zone 38 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04747 | Zone 38 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04748 | Zone 38 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04749 | Zone 38 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04750 | Zone 38 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04751 | Zone 38 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04752 | Zone 38 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04753 | Zone 38 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04754 | Zone 38 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04755 | Zone 38 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04756 | Zone 38 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04757 | Zone 38 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04801 | Zone 39 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04802 | Zone 39 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04803 | Zone 39 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04804 | Zone 39 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04805 | Zone 39 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04806 | Zone 39 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04807 | Zone 39 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04808 | Zone 39 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04809 | Zone 39 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04810 | Zone 39 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04811 | Zone 39 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04812 | Zone 39 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04813 | Zone 39 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04814 | Zone 39 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04815 | Zone 39 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04816 | Zone 39 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04817 | Zone 39 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04818 | Zone 39 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04819 | Zone 39 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04820 | Zone 39 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04821 | Zone 39 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04822 | Zone 39 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04823 | Zone 39 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04824 | Zone 39 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04825 | Zone 39 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04826 | Zone 39 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04827 | Zone 39 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04828 | Zone 39 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04829 | Zone 39 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04830 | Zone 39 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04831 | Zone 39 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04832 | Zone 39 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04833 | Zone 39 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04834 | Zone 39 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04835 | Zone 39 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04836 | Zone 39 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04837 | Zone 39 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04838 | Zone 39 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04839 | Zone 39 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04840 | Zone 39 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04841 | Zone 39 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04842 | Zone 39 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04843 | Zone 39 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04844 | Zone 39 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04845 | Zone 39 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04846 | Zone 39 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04847 | Zone 39 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04848 | Zone 39 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04849 | Zone 39 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04850 | Zone 39 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04851 | Zone 39 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04852 | Zone 39 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04853 | Zone 39 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04854 | Zone 39 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04855 | Zone 39 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04856 | Zone 39 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04857 | Zone 39 | Day 7 Event 3 End Time | 0 | 1440 | min
4:04901 | Zone 40 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:04902 | Zone 40 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:04903 | Zone 40 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:04904 | Zone 40 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04905 | Zone 40 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:04906 | Zone 40 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:04907 | Zone 40 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:04908 | Zone 40 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:04909 | Zone 40 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:04910 | Zone 40 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:04911 | Zone 40 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:04912 | Zone 40 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:04913 | Zone 40 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:04914 | Zone 40 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:04915 | Zone 40 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:04916 | Zone 40 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:04917 | Zone 40 | Day 1 Event 1 End Time | 0 | 1440 | min
4:04918 | Zone 40 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:04919 | Zone 40 | Day 1 Event 2 End Time | 0 | 1440 | min
4:04920 | Zone 40 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:04921 | Zone 40 | Day 1 Event 3 End Time | 0 | 1440 | min
4:04922 | Zone 40 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:04923 | Zone 40 | Day 2 Event 1 End Time | 0 | 1440 | min
4:04924 | Zone 40 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:04925 | Zone 40 | Day 2 Event 2 End Time | 0 | 1440 | min
4:04926 | Zone 40 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:04927 | Zone 40 | Day 2 Event 3 End Time | 0 | 1440 | min
4:04928 | Zone 40 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:04929 | Zone 40 | Day 3 Event 1 End Time | 0 | 1440 | min
4:04930 | Zone 40 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:04931 | Zone 40 | Day 3 Event 2 End Time | 0 | 1440 | min
4:04932 | Zone 40 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:04933 | Zone 40 | Day 3 Event 3 End Time | 0 | 1440 | min
4:04934 | Zone 40 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:04935 | Zone 40 | Day 4 Event 1 End Time | 0 | 1440 | min
4:04936 | Zone 40 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:04937 | Zone 40 | Day 4 Event 2 End Time | 0 | 1440 | min
4:04938 | Zone 40 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:04939 | Zone 40 | Day 4 Event 3 End Time | 0 | 1440 | min
4:04940 | Zone 40 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:04941 | Zone 40 | Day 5 Event 1 End Time | 0 | 1440 | min
4:04942 | Zone 40 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:04943 | Zone 40 | Day 5 Event 2 End Time | 0 | 1440 | min
4:04944 | Zone 40 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:04945 | Zone 40 | Day 5 Event 3 End Time | 0 | 1440 | min
4:04946 | Zone 40 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:04947 | Zone 40 | Day 6 Event 1 End Time | 0 | 1440 | min
4:04948 | Zone 40 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:04949 | Zone 40 | Day 6 Event 2 End Time | 0 | 1440 | min
4:04950 | Zone 40 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:04951 | Zone 40 | Day 6 Event 3 End Time | 0 | 1440 | min
4:04952 | Zone 40 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:04953 | Zone 40 | Day 7 Event 1 End Time | 0 | 1440 | min
4:04954 | Zone 40 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:04955 | Zone 40 | Day 7 Event 2 End Time | 0 | 1440 | min
4:04956 | Zone 40 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:04957 | Zone 40 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05001 | Zone 41 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05002 | Zone 41 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05003 | Zone 41 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05004 | Zone 41 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05005 | Zone 41 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05006 | Zone 41 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05007 | Zone 41 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05008 | Zone 41 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05009 | Zone 41 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05010 | Zone 41 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05011 | Zone 41 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05012 | Zone 41 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05013 | Zone 41 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05014 | Zone 41 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05015 | Zone 41 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05016 | Zone 41 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05017 | Zone 41 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05018 | Zone 41 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05019 | Zone 41 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05020 | Zone 41 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05021 | Zone 41 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05022 | Zone 41 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05023 | Zone 41 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05024 | Zone 41 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05025 | Zone 41 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05026 | Zone 41 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05027 | Zone 41 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05028 | Zone 41 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05029 | Zone 41 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05030 | Zone 41 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05031 | Zone 41 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05032 | Zone 41 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05033 | Zone 41 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05034 | Zone 41 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05035 | Zone 41 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05036 | Zone 41 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05037 | Zone 41 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05038 | Zone 41 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05039 | Zone 41 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05040 | Zone 41 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05041 | Zone 41 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05042 | Zone 41 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05043 | Zone 41 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05044 | Zone 41 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05045 | Zone 41 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05046 | Zone 41 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05047 | Zone 41 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05048 | Zone 41 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05049 | Zone 41 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05050 | Zone 41 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05051 | Zone 41 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05052 | Zone 41 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05053 | Zone 41 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05054 | Zone 41 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05055 | Zone 41 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05056 | Zone 41 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05057 | Zone 41 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05101 | Zone 42 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05102 | Zone 42 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05103 | Zone 42 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05104 | Zone 42 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05105 | Zone 42 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05106 | Zone 42 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05107 | Zone 42 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05108 | Zone 42 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05109 | Zone 42 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05110 | Zone 42 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05111 | Zone 42 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05112 | Zone 42 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05113 | Zone 42 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05114 | Zone 42 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05115 | Zone 42 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05116 | Zone 42 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05117 | Zone 42 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05118 | Zone 42 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05119 | Zone 42 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05120 | Zone 42 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05121 | Zone 42 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05122 | Zone 42 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05123 | Zone 42 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05124 | Zone 42 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05125 | Zone 42 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05126 | Zone 42 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05127 | Zone 42 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05128 | Zone 42 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05129 | Zone 42 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05130 | Zone 42 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05131 | Zone 42 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05132 | Zone 42 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05133 | Zone 42 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05134 | Zone 42 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05135 | Zone 42 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05136 | Zone 42 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05137 | Zone 42 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05138 | Zone 42 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05139 | Zone 42 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05140 | Zone 42 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05141 | Zone 42 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05142 | Zone 42 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05143 | Zone 42 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05144 | Zone 42 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05145 | Zone 42 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05146 | Zone 42 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05147 | Zone 42 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05148 | Zone 42 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05149 | Zone 42 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05150 | Zone 42 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05151 | Zone 42 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05152 | Zone 42 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05153 | Zone 42 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05154 | Zone 42 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05155 | Zone 42 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05156 | Zone 42 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05157 | Zone 42 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05201 | Zone 43 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05202 | Zone 43 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05203 | Zone 43 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05204 | Zone 43 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05205 | Zone 43 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05206 | Zone 43 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05207 | Zone 43 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05208 | Zone 43 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05209 | Zone 43 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05210 | Zone 43 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05211 | Zone 43 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05212 | Zone 43 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05213 | Zone 43 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05214 | Zone 43 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05215 | Zone 43 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05216 | Zone 43 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05217 | Zone 43 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05218 | Zone 43 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05219 | Zone 43 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05220 | Zone 43 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05221 | Zone 43 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05222 | Zone 43 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05223 | Zone 43 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05224 | Zone 43 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05225 | Zone 43 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05226 | Zone 43 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05227 | Zone 43 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05228 | Zone 43 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05229 | Zone 43 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05230 | Zone 43 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05231 | Zone 43 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05232 | Zone 43 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05233 | Zone 43 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05234 | Zone 43 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05235 | Zone 43 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05236 | Zone 43 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05237 | Zone 43 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05238 | Zone 43 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05239 | Zone 43 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05240 | Zone 43 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05241 | Zone 43 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05242 | Zone 43 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05243 | Zone 43 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05244 | Zone 43 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05245 | Zone 43 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05246 | Zone 43 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05247 | Zone 43 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05248 | Zone 43 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05249 | Zone 43 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05250 | Zone 43 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05251 | Zone 43 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05252 | Zone 43 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05253 | Zone 43 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05254 | Zone 43 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05255 | Zone 43 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05256 | Zone 43 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05257 | Zone 43 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05301 | Zone 44 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05302 | Zone 44 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05303 | Zone 44 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05304 | Zone 44 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05305 | Zone 44 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05306 | Zone 44 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05307 | Zone 44 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05308 | Zone 44 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05309 | Zone 44 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05310 | Zone 44 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05311 | Zone 44 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05312 | Zone 44 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05313 | Zone 44 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05314 | Zone 44 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05315 | Zone 44 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05316 | Zone 44 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05317 | Zone 44 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05318 | Zone 44 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05319 | Zone 44 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05320 | Zone 44 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05321 | Zone 44 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05322 | Zone 44 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05323 | Zone 44 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05324 | Zone 44 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05325 | Zone 44 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05326 | Zone 44 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05327 | Zone 44 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05328 | Zone 44 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05329 | Zone 44 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05330 | Zone 44 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05331 | Zone 44 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05332 | Zone 44 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05333 | Zone 44 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05334 | Zone 44 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05335 | Zone 44 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05336 | Zone 44 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05337 | Zone 44 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05338 | Zone 44 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05339 | Zone 44 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05340 | Zone 44 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05341 | Zone 44 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05342 | Zone 44 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05343 | Zone 44 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05344 | Zone 44 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05345 | Zone 44 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05346 | Zone 44 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05347 | Zone 44 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05348 | Zone 44 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05349 | Zone 44 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05350 | Zone 44 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05351 | Zone 44 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05352 | Zone 44 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05353 | Zone 44 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05354 | Zone 44 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05355 | Zone 44 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05356 | Zone 44 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05357 | Zone 44 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05401 | Zone 45 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05402 | Zone 45 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05403 | Zone 45 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05404 | Zone 45 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05405 | Zone 45 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05406 | Zone 45 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05407 | Zone 45 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05408 | Zone 45 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05409 | Zone 45 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05410 | Zone 45 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05411 | Zone 45 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05412 | Zone 45 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05413 | Zone 45 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05414 | Zone 45 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05415 | Zone 45 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05416 | Zone 45 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05417 | Zone 45 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05418 | Zone 45 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05419 | Zone 45 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05420 | Zone 45 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05421 | Zone 45 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05422 | Zone 45 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05423 | Zone 45 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05424 | Zone 45 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05425 | Zone 45 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05426 | Zone 45 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05427 | Zone 45 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05428 | Zone 45 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05429 | Zone 45 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05430 | Zone 45 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05431 | Zone 45 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05432 | Zone 45 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05433 | Zone 45 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05434 | Zone 45 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05435 | Zone 45 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05436 | Zone 45 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05437 | Zone 45 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05438 | Zone 45 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05439 | Zone 45 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05440 | Zone 45 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05441 | Zone 45 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05442 | Zone 45 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05443 | Zone 45 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05444 | Zone 45 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05445 | Zone 45 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05446 | Zone 45 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05447 | Zone 45 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05448 | Zone 45 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05449 | Zone 45 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05450 | Zone 45 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05451 | Zone 45 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05452 | Zone 45 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05453 | Zone 45 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05454 | Zone 45 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05455 | Zone 45 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05456 | Zone 45 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05457 | Zone 45 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05501 | Zone 46 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05502 | Zone 46 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05503 | Zone 46 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05504 | Zone 46 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05505 | Zone 46 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05506 | Zone 46 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05507 | Zone 46 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05508 | Zone 46 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05509 | Zone 46 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05510 | Zone 46 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05511 | Zone 46 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05512 | Zone 46 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05513 | Zone 46 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05514 | Zone 46 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05515 | Zone 46 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05516 | Zone 46 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05517 | Zone 46 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05518 | Zone 46 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05519 | Zone 46 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05520 | Zone 46 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05521 | Zone 46 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05522 | Zone 46 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05523 | Zone 46 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05524 | Zone 46 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05525 | Zone 46 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05526 | Zone 46 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05527 | Zone 46 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05528 | Zone 46 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05529 | Zone 46 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05530 | Zone 46 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05531 | Zone 46 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05532 | Zone 46 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05533 | Zone 46 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05534 | Zone 46 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05535 | Zone 46 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05536 | Zone 46 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05537 | Zone 46 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05538 | Zone 46 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05539 | Zone 46 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05540 | Zone 46 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05541 | Zone 46 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05542 | Zone 46 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05543 | Zone 46 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05544 | Zone 46 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05545 | Zone 46 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05546 | Zone 46 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05547 | Zone 46 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05548 | Zone 46 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05549 | Zone 46 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05550 | Zone 46 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05551 | Zone 46 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05552 | Zone 46 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05553 | Zone 46 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05554 | Zone 46 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05555 | Zone 46 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05556 | Zone 46 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05557 | Zone 46 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05601 | Zone 47 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05602 | Zone 47 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05603 | Zone 47 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05604 | Zone 47 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05605 | Zone 47 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05606 | Zone 47 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05607 | Zone 47 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05608 | Zone 47 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05609 | Zone 47 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05610 | Zone 47 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05611 | Zone 47 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05612 | Zone 47 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05613 | Zone 47 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05614 | Zone 47 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05615 | Zone 47 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05616 | Zone 47 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05617 | Zone 47 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05618 | Zone 47 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05619 | Zone 47 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05620 | Zone 47 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05621 | Zone 47 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05622 | Zone 47 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05623 | Zone 47 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05624 | Zone 47 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05625 | Zone 47 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05626 | Zone 47 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05627 | Zone 47 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05628 | Zone 47 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05629 | Zone 47 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05630 | Zone 47 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05631 | Zone 47 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05632 | Zone 47 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05633 | Zone 47 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05634 | Zone 47 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05635 | Zone 47 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05636 | Zone 47 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05637 | Zone 47 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05638 | Zone 47 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05639 | Zone 47 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05640 | Zone 47 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05641 | Zone 47 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05642 | Zone 47 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05643 | Zone 47 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05644 | Zone 47 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05645 | Zone 47 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05646 | Zone 47 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05647 | Zone 47 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05648 | Zone 47 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05649 | Zone 47 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05650 | Zone 47 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05651 | Zone 47 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05652 | Zone 47 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05653 | Zone 47 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05654 | Zone 47 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05655 | Zone 47 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05656 | Zone 47 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05657 | Zone 47 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05701 | Zone 48 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05702 | Zone 48 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05703 | Zone 48 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05704 | Zone 48 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05705 | Zone 48 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05706 | Zone 48 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05707 | Zone 48 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05708 | Zone 48 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05709 | Zone 48 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05710 | Zone 48 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05711 | Zone 48 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05712 | Zone 48 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05713 | Zone 48 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05714 | Zone 48 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05715 | Zone 48 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05716 | Zone 48 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05717 | Zone 48 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05718 | Zone 48 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05719 | Zone 48 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05720 | Zone 48 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05721 | Zone 48 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05722 | Zone 48 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05723 | Zone 48 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05724 | Zone 48 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05725 | Zone 48 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05726 | Zone 48 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05727 | Zone 48 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05728 | Zone 48 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05729 | Zone 48 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05730 | Zone 48 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05731 | Zone 48 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05732 | Zone 48 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05733 | Zone 48 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05734 | Zone 48 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05735 | Zone 48 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05736 | Zone 48 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05737 | Zone 48 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05738 | Zone 48 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05739 | Zone 48 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05740 | Zone 48 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05741 | Zone 48 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05742 | Zone 48 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05743 | Zone 48 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05744 | Zone 48 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05745 | Zone 48 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05746 | Zone 48 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05747 | Zone 48 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05748 | Zone 48 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05749 | Zone 48 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05750 | Zone 48 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05751 | Zone 48 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05752 | Zone 48 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05753 | Zone 48 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05754 | Zone 48 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05755 | Zone 48 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05756 | Zone 48 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05757 | Zone 48 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05801 | Zone 49 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05802 | Zone 49 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05803 | Zone 49 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05804 | Zone 49 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05805 | Zone 49 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05806 | Zone 49 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05807 | Zone 49 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05808 | Zone 49 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05809 | Zone 49 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05810 | Zone 49 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05811 | Zone 49 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05812 | Zone 49 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05813 | Zone 49 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05814 | Zone 49 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05815 | Zone 49 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05816 | Zone 49 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05817 | Zone 49 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05818 | Zone 49 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05819 | Zone 49 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05820 | Zone 49 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05821 | Zone 49 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05822 | Zone 49 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05823 | Zone 49 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05824 | Zone 49 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05825 | Zone 49 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05826 | Zone 49 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05827 | Zone 49 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05828 | Zone 49 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05829 | Zone 49 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05830 | Zone 49 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05831 | Zone 49 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05832 | Zone 49 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05833 | Zone 49 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05834 | Zone 49 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05835 | Zone 49 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05836 | Zone 49 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05837 | Zone 49 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05838 | Zone 49 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05839 | Zone 49 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05840 | Zone 49 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05841 | Zone 49 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05842 | Zone 49 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05843 | Zone 49 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05844 | Zone 49 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05845 | Zone 49 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05846 | Zone 49 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05847 | Zone 49 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05848 | Zone 49 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05849 | Zone 49 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05850 | Zone 49 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05851 | Zone 49 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05852 | Zone 49 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05853 | Zone 49 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05854 | Zone 49 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05855 | Zone 49 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05856 | Zone 49 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05857 | Zone 49 | Day 7 Event 3 End Time | 0 | 1440 | min
4:05901 | Zone 50 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:05902 | Zone 50 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:05903 | Zone 50 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:05904 | Zone 50 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05905 | Zone 50 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:05906 | Zone 50 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:05907 | Zone 50 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:05908 | Zone 50 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:05909 | Zone 50 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:05910 | Zone 50 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:05911 | Zone 50 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:05912 | Zone 50 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:05913 | Zone 50 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:05914 | Zone 50 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:05915 | Zone 50 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:05916 | Zone 50 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:05917 | Zone 50 | Day 1 Event 1 End Time | 0 | 1440 | min
4:05918 | Zone 50 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:05919 | Zone 50 | Day 1 Event 2 End Time | 0 | 1440 | min
4:05920 | Zone 50 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:05921 | Zone 50 | Day 1 Event 3 End Time | 0 | 1440 | min
4:05922 | Zone 50 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:05923 | Zone 50 | Day 2 Event 1 End Time | 0 | 1440 | min
4:05924 | Zone 50 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:05925 | Zone 50 | Day 2 Event 2 End Time | 0 | 1440 | min
4:05926 | Zone 50 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:05927 | Zone 50 | Day 2 Event 3 End Time | 0 | 1440 | min
4:05928 | Zone 50 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:05929 | Zone 50 | Day 3 Event 1 End Time | 0 | 1440 | min
4:05930 | Zone 50 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:05931 | Zone 50 | Day 3 Event 2 End Time | 0 | 1440 | min
4:05932 | Zone 50 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:05933 | Zone 50 | Day 3 Event 3 End Time | 0 | 1440 | min
4:05934 | Zone 50 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:05935 | Zone 50 | Day 4 Event 1 End Time | 0 | 1440 | min
4:05936 | Zone 50 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:05937 | Zone 50 | Day 4 Event 2 End Time | 0 | 1440 | min
4:05938 | Zone 50 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:05939 | Zone 50 | Day 4 Event 3 End Time | 0 | 1440 | min
4:05940 | Zone 50 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:05941 | Zone 50 | Day 5 Event 1 End Time | 0 | 1440 | min
4:05942 | Zone 50 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:05943 | Zone 50 | Day 5 Event 2 End Time | 0 | 1440 | min
4:05944 | Zone 50 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:05945 | Zone 50 | Day 5 Event 3 End Time | 0 | 1440 | min
4:05946 | Zone 50 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:05947 | Zone 50 | Day 6 Event 1 End Time | 0 | 1440 | min
4:05948 | Zone 50 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:05949 | Zone 50 | Day 6 Event 2 End Time | 0 | 1440 | min
4:05950 | Zone 50 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:05951 | Zone 50 | Day 6 Event 3 End Time | 0 | 1440 | min
4:05952 | Zone 50 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:05953 | Zone 50 | Day 7 Event 1 End Time | 0 | 1440 | min
4:05954 | Zone 50 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:05955 | Zone 50 | Day 7 Event 2 End Time | 0 | 1440 | min
4:05956 | Zone 50 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:05957 | Zone 50 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06001 | Zone 51 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06002 | Zone 51 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06003 | Zone 51 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06004 | Zone 51 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06005 | Zone 51 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06006 | Zone 51 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06007 | Zone 51 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06008 | Zone 51 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06009 | Zone 51 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06010 | Zone 51 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06011 | Zone 51 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06012 | Zone 51 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06013 | Zone 51 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06014 | Zone 51 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06015 | Zone 51 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06016 | Zone 51 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06017 | Zone 51 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06018 | Zone 51 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06019 | Zone 51 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06020 | Zone 51 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06021 | Zone 51 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06022 | Zone 51 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06023 | Zone 51 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06024 | Zone 51 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06025 | Zone 51 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06026 | Zone 51 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06027 | Zone 51 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06028 | Zone 51 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06029 | Zone 51 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06030 | Zone 51 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06031 | Zone 51 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06032 | Zone 51 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06033 | Zone 51 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06034 | Zone 51 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06035 | Zone 51 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06036 | Zone 51 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06037 | Zone 51 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06038 | Zone 51 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06039 | Zone 51 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06040 | Zone 51 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06041 | Zone 51 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06042 | Zone 51 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06043 | Zone 51 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06044 | Zone 51 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06045 | Zone 51 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06046 | Zone 51 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06047 | Zone 51 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06048 | Zone 51 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06049 | Zone 51 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06050 | Zone 51 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06051 | Zone 51 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06052 | Zone 51 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06053 | Zone 51 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06054 | Zone 51 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06055 | Zone 51 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06056 | Zone 51 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06057 | Zone 51 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06101 | Zone 52 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06102 | Zone 52 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06103 | Zone 52 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06104 | Zone 52 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06105 | Zone 52 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06106 | Zone 52 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06107 | Zone 52 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06108 | Zone 52 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06109 | Zone 52 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06110 | Zone 52 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06111 | Zone 52 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06112 | Zone 52 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06113 | Zone 52 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06114 | Zone 52 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06115 | Zone 52 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06116 | Zone 52 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06117 | Zone 52 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06118 | Zone 52 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06119 | Zone 52 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06120 | Zone 52 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06121 | Zone 52 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06122 | Zone 52 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06123 | Zone 52 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06124 | Zone 52 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06125 | Zone 52 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06126 | Zone 52 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06127 | Zone 52 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06128 | Zone 52 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06129 | Zone 52 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06130 | Zone 52 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06131 | Zone 52 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06132 | Zone 52 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06133 | Zone 52 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06134 | Zone 52 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06135 | Zone 52 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06136 | Zone 52 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06137 | Zone 52 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06138 | Zone 52 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06139 | Zone 52 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06140 | Zone 52 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06141 | Zone 52 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06142 | Zone 52 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06143 | Zone 52 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06144 | Zone 52 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06145 | Zone 52 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06146 | Zone 52 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06147 | Zone 52 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06148 | Zone 52 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06149 | Zone 52 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06150 | Zone 52 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06151 | Zone 52 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06152 | Zone 52 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06153 | Zone 52 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06154 | Zone 52 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06155 | Zone 52 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06156 | Zone 52 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06157 | Zone 52 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06201 | Zone 53 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06202 | Zone 53 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06203 | Zone 53 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06204 | Zone 53 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06205 | Zone 53 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06206 | Zone 53 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06207 | Zone 53 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06208 | Zone 53 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06209 | Zone 53 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06210 | Zone 53 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06211 | Zone 53 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06212 | Zone 53 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06213 | Zone 53 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06214 | Zone 53 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06215 | Zone 53 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06216 | Zone 53 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06217 | Zone 53 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06218 | Zone 53 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06219 | Zone 53 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06220 | Zone 53 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06221 | Zone 53 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06222 | Zone 53 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06223 | Zone 53 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06224 | Zone 53 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06225 | Zone 53 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06226 | Zone 53 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06227 | Zone 53 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06228 | Zone 53 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06229 | Zone 53 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06230 | Zone 53 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06231 | Zone 53 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06232 | Zone 53 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06233 | Zone 53 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06234 | Zone 53 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06235 | Zone 53 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06236 | Zone 53 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06237 | Zone 53 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06238 | Zone 53 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06239 | Zone 53 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06240 | Zone 53 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06241 | Zone 53 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06242 | Zone 53 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06243 | Zone 53 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06244 | Zone 53 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06245 | Zone 53 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06246 | Zone 53 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06247 | Zone 53 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06248 | Zone 53 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06249 | Zone 53 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06250 | Zone 53 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06251 | Zone 53 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06252 | Zone 53 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06253 | Zone 53 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06254 | Zone 53 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06255 | Zone 53 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06256 | Zone 53 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06257 | Zone 53 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06301 | Zone 54 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06302 | Zone 54 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06303 | Zone 54 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06304 | Zone 54 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06305 | Zone 54 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06306 | Zone 54 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06307 | Zone 54 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06308 | Zone 54 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06309 | Zone 54 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06310 | Zone 54 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06311 | Zone 54 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06312 | Zone 54 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06313 | Zone 54 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06314 | Zone 54 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06315 | Zone 54 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06316 | Zone 54 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06317 | Zone 54 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06318 | Zone 54 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06319 | Zone 54 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06320 | Zone 54 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06321 | Zone 54 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06322 | Zone 54 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06323 | Zone 54 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06324 | Zone 54 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06325 | Zone 54 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06326 | Zone 54 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06327 | Zone 54 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06328 | Zone 54 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06329 | Zone 54 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06330 | Zone 54 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06331 | Zone 54 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06332 | Zone 54 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06333 | Zone 54 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06334 | Zone 54 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06335 | Zone 54 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06336 | Zone 54 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06337 | Zone 54 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06338 | Zone 54 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06339 | Zone 54 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06340 | Zone 54 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06341 | Zone 54 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06342 | Zone 54 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06343 | Zone 54 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06344 | Zone 54 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06345 | Zone 54 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06346 | Zone 54 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06347 | Zone 54 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06348 | Zone 54 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06349 | Zone 54 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06350 | Zone 54 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06351 | Zone 54 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06352 | Zone 54 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06353 | Zone 54 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06354 | Zone 54 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06355 | Zone 54 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06356 | Zone 54 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06357 | Zone 54 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06401 | Zone 55 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06402 | Zone 55 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06403 | Zone 55 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06404 | Zone 55 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06405 | Zone 55 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06406 | Zone 55 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06407 | Zone 55 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06408 | Zone 55 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06409 | Zone 55 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06410 | Zone 55 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06411 | Zone 55 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06412 | Zone 55 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06413 | Zone 55 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06414 | Zone 55 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06415 | Zone 55 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06416 | Zone 55 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06417 | Zone 55 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06418 | Zone 55 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06419 | Zone 55 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06420 | Zone 55 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06421 | Zone 55 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06422 | Zone 55 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06423 | Zone 55 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06424 | Zone 55 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06425 | Zone 55 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06426 | Zone 55 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06427 | Zone 55 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06428 | Zone 55 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06429 | Zone 55 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06430 | Zone 55 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06431 | Zone 55 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06432 | Zone 55 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06433 | Zone 55 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06434 | Zone 55 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06435 | Zone 55 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06436 | Zone 55 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06437 | Zone 55 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06438 | Zone 55 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06439 | Zone 55 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06440 | Zone 55 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06441 | Zone 55 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06442 | Zone 55 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06443 | Zone 55 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06444 | Zone 55 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06445 | Zone 55 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06446 | Zone 55 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06447 | Zone 55 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06448 | Zone 55 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06449 | Zone 55 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06450 | Zone 55 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06451 | Zone 55 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06452 | Zone 55 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06453 | Zone 55 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06454 | Zone 55 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06455 | Zone 55 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06456 | Zone 55 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06457 | Zone 55 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06501 | Zone 56 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06502 | Zone 56 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06503 | Zone 56 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06504 | Zone 56 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06505 | Zone 56 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06506 | Zone 56 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06507 | Zone 56 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06508 | Zone 56 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06509 | Zone 56 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06510 | Zone 56 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06511 | Zone 56 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06512 | Zone 56 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06513 | Zone 56 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06514 | Zone 56 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06515 | Zone 56 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06516 | Zone 56 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06517 | Zone 56 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06518 | Zone 56 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06519 | Zone 56 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06520 | Zone 56 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06521 | Zone 56 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06522 | Zone 56 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06523 | Zone 56 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06524 | Zone 56 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06525 | Zone 56 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06526 | Zone 56 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06527 | Zone 56 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06528 | Zone 56 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06529 | Zone 56 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06530 | Zone 56 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06531 | Zone 56 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06532 | Zone 56 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06533 | Zone 56 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06534 | Zone 56 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06535 | Zone 56 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06536 | Zone 56 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06537 | Zone 56 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06538 | Zone 56 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06539 | Zone 56 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06540 | Zone 56 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06541 | Zone 56 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06542 | Zone 56 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06543 | Zone 56 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06544 | Zone 56 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06545 | Zone 56 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06546 | Zone 56 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06547 | Zone 56 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06548 | Zone 56 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06549 | Zone 56 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06550 | Zone 56 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06551 | Zone 56 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06552 | Zone 56 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06553 | Zone 56 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06554 | Zone 56 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06555 | Zone 56 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06556 | Zone 56 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06557 | Zone 56 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06601 | Zone 57 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06602 | Zone 57 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06603 | Zone 57 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06604 | Zone 57 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06605 | Zone 57 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06606 | Zone 57 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06607 | Zone 57 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06608 | Zone 57 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06609 | Zone 57 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06610 | Zone 57 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06611 | Zone 57 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06612 | Zone 57 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06613 | Zone 57 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06614 | Zone 57 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06615 | Zone 57 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06616 | Zone 57 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06617 | Zone 57 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06618 | Zone 57 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06619 | Zone 57 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06620 | Zone 57 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06621 | Zone 57 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06622 | Zone 57 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06623 | Zone 57 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06624 | Zone 57 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06625 | Zone 57 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06626 | Zone 57 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06627 | Zone 57 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06628 | Zone 57 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06629 | Zone 57 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06630 | Zone 57 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06631 | Zone 57 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06632 | Zone 57 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06633 | Zone 57 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06634 | Zone 57 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06635 | Zone 57 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06636 | Zone 57 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06637 | Zone 57 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06638 | Zone 57 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06639 | Zone 57 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06640 | Zone 57 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06641 | Zone 57 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06642 | Zone 57 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06643 | Zone 57 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06644 | Zone 57 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06645 | Zone 57 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06646 | Zone 57 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06647 | Zone 57 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06648 | Zone 57 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06649 | Zone 57 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06650 | Zone 57 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06651 | Zone 57 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06652 | Zone 57 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06653 | Zone 57 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06654 | Zone 57 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06655 | Zone 57 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06656 | Zone 57 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06657 | Zone 57 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06701 | Zone 58 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06702 | Zone 58 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06703 | Zone 58 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06704 | Zone 58 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06705 | Zone 58 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06706 | Zone 58 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06707 | Zone 58 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06708 | Zone 58 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06709 | Zone 58 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06710 | Zone 58 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06711 | Zone 58 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06712 | Zone 58 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06713 | Zone 58 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06714 | Zone 58 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06715 | Zone 58 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06716 | Zone 58 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06717 | Zone 58 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06718 | Zone 58 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06719 | Zone 58 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06720 | Zone 58 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06721 | Zone 58 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06722 | Zone 58 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06723 | Zone 58 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06724 | Zone 58 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06725 | Zone 58 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06726 | Zone 58 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06727 | Zone 58 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06728 | Zone 58 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06729 | Zone 58 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06730 | Zone 58 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06731 | Zone 58 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06732 | Zone 58 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06733 | Zone 58 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06734 | Zone 58 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06735 | Zone 58 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06736 | Zone 58 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06737 | Zone 58 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06738 | Zone 58 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06739 | Zone 58 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06740 | Zone 58 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06741 | Zone 58 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06742 | Zone 58 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06743 | Zone 58 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06744 | Zone 58 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06745 | Zone 58 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06746 | Zone 58 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06747 | Zone 58 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06748 | Zone 58 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06749 | Zone 58 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06750 | Zone 58 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06751 | Zone 58 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06752 | Zone 58 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06753 | Zone 58 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06754 | Zone 58 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06755 | Zone 58 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06756 | Zone 58 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06757 | Zone 58 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06801 | Zone 59 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06802 | Zone 59 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06803 | Zone 59 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06804 | Zone 59 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06805 | Zone 59 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06806 | Zone 59 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06807 | Zone 59 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06808 | Zone 59 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06809 | Zone 59 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06810 | Zone 59 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06811 | Zone 59 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06812 | Zone 59 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06813 | Zone 59 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06814 | Zone 59 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06815 | Zone 59 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06816 | Zone 59 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06817 | Zone 59 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06818 | Zone 59 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06819 | Zone 59 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06820 | Zone 59 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06821 | Zone 59 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06822 | Zone 59 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06823 | Zone 59 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06824 | Zone 59 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06825 | Zone 59 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06826 | Zone 59 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06827 | Zone 59 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06828 | Zone 59 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06829 | Zone 59 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06830 | Zone 59 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06831 | Zone 59 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06832 | Zone 59 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06833 | Zone 59 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06834 | Zone 59 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06835 | Zone 59 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06836 | Zone 59 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06837 | Zone 59 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06838 | Zone 59 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06839 | Zone 59 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06840 | Zone 59 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06841 | Zone 59 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06842 | Zone 59 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06843 | Zone 59 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06844 | Zone 59 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06845 | Zone 59 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06846 | Zone 59 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06847 | Zone 59 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06848 | Zone 59 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06849 | Zone 59 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06850 | Zone 59 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06851 | Zone 59 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06852 | Zone 59 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06853 | Zone 59 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06854 | Zone 59 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06855 | Zone 59 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06856 | Zone 59 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06857 | Zone 59 | Day 7 Event 3 End Time | 0 | 1440 | min
4:06901 | Zone 60 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:06902 | Zone 60 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:06903 | Zone 60 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:06904 | Zone 60 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06905 | Zone 60 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:06906 | Zone 60 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:06907 | Zone 60 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:06908 | Zone 60 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:06909 | Zone 60 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:06910 | Zone 60 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:06911 | Zone 60 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:06912 | Zone 60 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:06913 | Zone 60 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:06914 | Zone 60 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:06915 | Zone 60 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:06916 | Zone 60 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:06917 | Zone 60 | Day 1 Event 1 End Time | 0 | 1440 | min
4:06918 | Zone 60 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:06919 | Zone 60 | Day 1 Event 2 End Time | 0 | 1440 | min
4:06920 | Zone 60 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:06921 | Zone 60 | Day 1 Event 3 End Time | 0 | 1440 | min
4:06922 | Zone 60 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:06923 | Zone 60 | Day 2 Event 1 End Time | 0 | 1440 | min
4:06924 | Zone 60 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:06925 | Zone 60 | Day 2 Event 2 End Time | 0 | 1440 | min
4:06926 | Zone 60 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:06927 | Zone 60 | Day 2 Event 3 End Time | 0 | 1440 | min
4:06928 | Zone 60 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:06929 | Zone 60 | Day 3 Event 1 End Time | 0 | 1440 | min
4:06930 | Zone 60 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:06931 | Zone 60 | Day 3 Event 2 End Time | 0 | 1440 | min
4:06932 | Zone 60 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:06933 | Zone 60 | Day 3 Event 3 End Time | 0 | 1440 | min
4:06934 | Zone 60 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:06935 | Zone 60 | Day 4 Event 1 End Time | 0 | 1440 | min
4:06936 | Zone 60 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:06937 | Zone 60 | Day 4 Event 2 End Time | 0 | 1440 | min
4:06938 | Zone 60 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:06939 | Zone 60 | Day 4 Event 3 End Time | 0 | 1440 | min
4:06940 | Zone 60 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:06941 | Zone 60 | Day 5 Event 1 End Time | 0 | 1440 | min
4:06942 | Zone 60 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:06943 | Zone 60 | Day 5 Event 2 End Time | 0 | 1440 | min
4:06944 | Zone 60 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:06945 | Zone 60 | Day 5 Event 3 End Time | 0 | 1440 | min
4:06946 | Zone 60 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:06947 | Zone 60 | Day 6 Event 1 End Time | 0 | 1440 | min
4:06948 | Zone 60 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:06949 | Zone 60 | Day 6 Event 2 End Time | 0 | 1440 | min
4:06950 | Zone 60 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:06951 | Zone 60 | Day 6 Event 3 End Time | 0 | 1440 | min
4:06952 | Zone 60 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:06953 | Zone 60 | Day 7 Event 1 End Time | 0 | 1440 | min
4:06954 | Zone 60 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:06955 | Zone 60 | Day 7 Event 2 End Time | 0 | 1440 | min
4:06956 | Zone 60 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:06957 | Zone 60 | Day 7 Event 3 End Time | 0 | 1440 | min
4:07001 | Zone 61 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:07002 | Zone 61 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:07003 | Zone 61 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:07004 | Zone 61 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07005 | Zone 61 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07006 | Zone 61 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:07007 | Zone 61 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:07008 | Zone 61 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:07009 | Zone 61 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:07010 | Zone 61 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:07011 | Zone 61 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:07012 | Zone 61 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:07013 | Zone 61 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:07014 | Zone 61 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:07015 | Zone 61 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:07016 | Zone 61 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:07017 | Zone 61 | Day 1 Event 1 End Time | 0 | 1440 | min
4:07018 | Zone 61 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:07019 | Zone 61 | Day 1 Event 2 End Time | 0 | 1440 | min
4:07020 | Zone 61 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:07021 | Zone 61 | Day 1 Event 3 End Time | 0 | 1440 | min
4:07022 | Zone 61 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:07023 | Zone 61 | Day 2 Event 1 End Time | 0 | 1440 | min
4:07024 | Zone 61 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:07025 | Zone 61 | Day 2 Event 2 End Time | 0 | 1440 | min
4:07026 | Zone 61 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:07027 | Zone 61 | Day 2 Event 3 End Time | 0 | 1440 | min
4:07028 | Zone 61 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:07029 | Zone 61 | Day 3 Event 1 End Time | 0 | 1440 | min
4:07030 | Zone 61 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:07031 | Zone 61 | Day 3 Event 2 End Time | 0 | 1440 | min
4:07032 | Zone 61 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:07033 | Zone 61 | Day 3 Event 3 End Time | 0 | 1440 | min
4:07034 | Zone 61 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:07035 | Zone 61 | Day 4 Event 1 End Time | 0 | 1440 | min
4:07036 | Zone 61 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:07037 | Zone 61 | Day 4 Event 2 End Time | 0 | 1440 | min
4:07038 | Zone 61 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:07039 | Zone 61 | Day 4 Event 3 End Time | 0 | 1440 | min
4:07040 | Zone 61 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:07041 | Zone 61 | Day 5 Event 1 End Time | 0 | 1440 | min
4:07042 | Zone 61 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:07043 | Zone 61 | Day 5 Event 2 End Time | 0 | 1440 | min
4:07044 | Zone 61 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:07045 | Zone 61 | Day 5 Event 3 End Time | 0 | 1440 | min
4:07046 | Zone 61 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:07047 | Zone 61 | Day 6 Event 1 End Time | 0 | 1440 | min
4:07048 | Zone 61 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:07049 | Zone 61 | Day 6 Event 2 End Time | 0 | 1440 | min
4:07050 | Zone 61 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:07051 | Zone 61 | Day 6 Event 3 End Time | 0 | 1440 | min
4:07052 | Zone 61 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:07053 | Zone 61 | Day 7 Event 1 End Time | 0 | 1440 | min
4:07054 | Zone 61 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:07055 | Zone 61 | Day 7 Event 2 End Time | 0 | 1440 | min
4:07056 | Zone 61 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:07057 | Zone 61 | Day 7 Event 3 End Time | 0 | 1440 | min
4:07101 | Zone 62 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:07102 | Zone 62 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:07103 | Zone 62 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:07104 | Zone 62 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07105 | Zone 62 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07106 | Zone 62 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:07107 | Zone 62 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:07108 | Zone 62 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:07109 | Zone 62 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:07110 | Zone 62 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:07111 | Zone 62 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:07112 | Zone 62 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:07113 | Zone 62 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:07114 | Zone 62 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:07115 | Zone 62 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:07116 | Zone 62 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:07117 | Zone 62 | Day 1 Event 1 End Time | 0 | 1440 | min
4:07118 | Zone 62 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:07119 | Zone 62 | Day 1 Event 2 End Time | 0 | 1440 | min
4:07120 | Zone 62 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:07121 | Zone 62 | Day 1 Event 3 End Time | 0 | 1440 | min
4:07122 | Zone 62 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:07123 | Zone 62 | Day 2 Event 1 End Time | 0 | 1440 | min
4:07124 | Zone 62 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:07125 | Zone 62 | Day 2 Event 2 End Time | 0 | 1440 | min
4:07126 | Zone 62 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:07127 | Zone 62 | Day 2 Event 3 End Time | 0 | 1440 | min
4:07128 | Zone 62 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:07129 | Zone 62 | Day 3 Event 1 End Time | 0 | 1440 | min
4:07130 | Zone 62 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:07131 | Zone 62 | Day 3 Event 2 End Time | 0 | 1440 | min
4:07132 | Zone 62 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:07133 | Zone 62 | Day 3 Event 3 End Time | 0 | 1440 | min
4:07134 | Zone 62 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:07135 | Zone 62 | Day 4 Event 1 End Time | 0 | 1440 | min
4:07136 | Zone 62 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:07137 | Zone 62 | Day 4 Event 2 End Time | 0 | 1440 | min
4:07138 | Zone 62 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:07139 | Zone 62 | Day 4 Event 3 End Time | 0 | 1440 | min
4:07140 | Zone 62 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:07141 | Zone 62 | Day 5 Event 1 End Time | 0 | 1440 | min
4:07142 | Zone 62 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:07143 | Zone 62 | Day 5 Event 2 End Time | 0 | 1440 | min
4:07144 | Zone 62 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:07145 | Zone 62 | Day 5 Event 3 End Time | 0 | 1440 | min
4:07146 | Zone 62 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:07147 | Zone 62 | Day 6 Event 1 End Time | 0 | 1440 | min
4:07148 | Zone 62 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:07149 | Zone 62 | Day 6 Event 2 End Time | 0 | 1440 | min
4:07150 | Zone 62 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:07151 | Zone 62 | Day 6 Event 3 End Time | 0 | 1440 | min
4:07152 | Zone 62 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:07153 | Zone 62 | Day 7 Event 1 End Time | 0 | 1440 | min
4:07154 | Zone 62 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:07155 | Zone 62 | Day 7 Event 2 End Time | 0 | 1440 | min
4:07156 | Zone 62 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:07157 | Zone 62 | Day 7 Event 3 End Time | 0 | 1440 | min
4:07201 | Zone 63 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:07202 | Zone 63 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:07203 | Zone 63 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:07204 | Zone 63 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07205 | Zone 63 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07206 | Zone 63 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:07207 | Zone 63 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:07208 | Zone 63 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:07209 | Zone 63 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:07210 | Zone 63 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:07211 | Zone 63 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:07212 | Zone 63 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:07213 | Zone 63 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:07214 | Zone 63 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:07215 | Zone 63 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:07216 | Zone 63 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:07217 | Zone 63 | Day 1 Event 1 End Time | 0 | 1440 | min
4:07218 | Zone 63 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:07219 | Zone 63 | Day 1 Event 2 End Time | 0 | 1440 | min
4:07220 | Zone 63 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:07221 | Zone 63 | Day 1 Event 3 End Time | 0 | 1440 | min
4:07222 | Zone 63 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:07223 | Zone 63 | Day 2 Event 1 End Time | 0 | 1440 | min
4:07224 | Zone 63 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:07225 | Zone 63 | Day 2 Event 2 End Time | 0 | 1440 | min
4:07226 | Zone 63 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:07227 | Zone 63 | Day 2 Event 3 End Time | 0 | 1440 | min
4:07228 | Zone 63 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:07229 | Zone 63 | Day 3 Event 1 End Time | 0 | 1440 | min
4:07230 | Zone 63 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:07231 | Zone 63 | Day 3 Event 2 End Time | 0 | 1440 | min
4:07232 | Zone 63 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:07233 | Zone 63 | Day 3 Event 3 End Time | 0 | 1440 | min
4:07234 | Zone 63 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:07235 | Zone 63 | Day 4 Event 1 End Time | 0 | 1440 | min
4:07236 | Zone 63 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:07237 | Zone 63 | Day 4 Event 2 End Time | 0 | 1440 | min
4:07238 | Zone 63 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:07239 | Zone 63 | Day 4 Event 3 End Time | 0 | 1440 | min
4:07240 | Zone 63 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:07241 | Zone 63 | Day 5 Event 1 End Time | 0 | 1440 | min
4:07242 | Zone 63 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:07243 | Zone 63 | Day 5 Event 2 End Time | 0 | 1440 | min
4:07244 | Zone 63 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:07245 | Zone 63 | Day 5 Event 3 End Time | 0 | 1440 | min
4:07246 | Zone 63 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:07247 | Zone 63 | Day 6 Event 1 End Time | 0 | 1440 | min
4:07248 | Zone 63 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:07249 | Zone 63 | Day 6 Event 2 End Time | 0 | 1440 | min
4:07250 | Zone 63 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:07251 | Zone 63 | Day 6 Event 3 End Time | 0 | 1440 | min
4:07252 | Zone 63 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:07253 | Zone 63 | Day 7 Event 1 End Time | 0 | 1440 | min
4:07254 | Zone 63 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:07255 | Zone 63 | Day 7 Event 2 End Time | 0 | 1440 | min
4:07256 | Zone 63 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:07257 | Zone 63 | Day 7 Event 3 End Time | 0 | 1440 | min
4:07301 | Zone 64 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:07302 | Zone 64 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:07303 | Zone 64 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:07304 | Zone 64 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07305 | Zone 64 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:07306 | Zone 64 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:07307 | Zone 64 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:07308 | Zone 64 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:07309 | Zone 64 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:07310 | Zone 64 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:07311 | Zone 64 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:07312 | Zone 64 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:07313 | Zone 64 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:07314 | Zone 64 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:07315 | Zone 64 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:07316 | Zone 64 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:07317 | Zone 64 | Day 1 Event 1 End Time | 0 | 1440 | min
4:07318 | Zone 64 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:07319 | Zone 64 | Day 1 Event 2 End Time | 0 | 1440 | min
4:07320 | Zone 64 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:07321 | Zone 64 | Day 1 Event 3 End Time | 0 | 1440 | min
4:07322 | Zone 64 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:07323 | Zone 64 | Day 2 Event 1 End Time | 0 | 1440 | min
4:07324 | Zone 64 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:07325 | Zone 64 | Day 2 Event 2 End Time | 0 | 1440 | min
4:07326 | Zone 64 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:07327 | Zone 64 | Day 2 Event 3 End Time | 0 | 1440 | min
4:07328 | Zone 64 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:07329 | Zone 64 | Day 3 Event 1 End Time | 0 | 1440 | min
4:07330 | Zone 64 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:07331 | Zone 64 | Day 3 Event 2 End Time | 0 | 1440 | min
4:07332 | Zone 64 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:07333 | Zone 64 | Day 3 Event 3 End Time | 0 | 1440 | min
4:07334 | Zone 64 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:07335 | Zone 64 | Day 4 Event 1 End Time | 0 | 1440 | min
4:07336 | Zone 64 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:07337 | Zone 64 | Day 4 Event 2 End Time | 0 | 1440 | min
4:07338 | Zone 64 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:07339 | Zone 64 | Day 4 Event 3 End Time | 0 | 1440 | min
4:07340 | Zone 64 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:07341 | Zone 64 | Day 5 Event 1 End Time | 0 | 1440 | min
4:07342 | Zone 64 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:07343 | Zone 64 | Day 5 Event 2 End Time | 0 | 1440 | min
4:07344 | Zone 64 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:07345 | Zone 64 | Day 5 Event 3 End Time | 0 | 1440 | min
4:07346 | Zone 64 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:07347 | Zone 64 | Day 6 Event 1 End Time | 0 | 1440 | min
4:07348 | Zone 64 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:07349 | Zone 64 | Day 6 Event 2 End Time | 0 | 1440 | min
4:07350 | Zone 64 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:07351 | Zone 64 | Day 6 Event 3 End Time | 0 | 1440 | min
4:07352 | Zone 64 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:07353 | Zone 64 | Day 7 Event 1 End Time | 0 | 1440 | min
4:07354 | Zone 64 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:07355 | Zone 64 | Day 7 Event 2 End Time | 0 | 1440 | min
4:07356 | Zone 64 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:07357 | Zone 64 | Day 7 Event 3 End Time | 0 | 1440 | min
4:11001 | Zone 1 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11002 | Zone 2 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11003 | Zone 3 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11004 | Zone 4 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11005 | Zone 5 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11006 | Zone 6 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11007 | Zone 7 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11008 | Zone 8 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11009 | Zone 9 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11010 | Zone 10 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11011 | Zone 11 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11012 | Zone 12 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11013 | Zone 13 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11014 | Zone 14 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11015 | Zone 15 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11016 | Zone 16 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11017 | Zone 17 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11018 | Zone 18 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11019 | Zone 19 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11020 | Zone 20 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11021 | Zone 21 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11022 | Zone 22 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11023 | Zone 23 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11024 | Zone 24 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11025 | Zone 25 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11026 | Zone 26 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11027 | Zone 27 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11028 | Zone 28 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11029 | Zone 29 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11030 | Zone 30 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11031 | Zone 31 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11032 | Zone 32 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11033 | Zone 33 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11034 | Zone 34 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11035 | Zone 35 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11036 | Zone 36 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11037 | Zone 37 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11038 | Zone 38 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11039 | Zone 39 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11040 | Zone 40 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11041 | Zone 41 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11042 | Zone 42 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11043 | Zone 43 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11044 | Zone 44 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11045 | Zone 45 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11046 | Zone 46 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11047 | Zone 47 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11048 | Zone 48 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11049 | Zone 49 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11050 | Zone 50 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11051 | Zone 51 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11052 | Zone 52 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11053 | Zone 53 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11054 | Zone 54 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11055 | Zone 55 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11056 | Zone 56 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11057 | Zone 57 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11058 | Zone 58 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11059 | Zone 59 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11060 | Zone 60 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11061 | Zone 61 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11062 | Zone 62 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11063 | Zone 63 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11064 | Zone 64 | Fireplace Compensation Control | 0 | 100 | h | Fireplace Compensation: 0 - Off, 1-99 - Active for N hours, 100 - Always On.
4:11065 | Zone 1 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11066 | Zone 2 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11067 | Zone 3 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11068 | Zone 4 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11069 | Zone 5 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11070 | Zone 6 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11071 | Zone 7 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11072 | Zone 8 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11073 | Zone 9 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11074 | Zone 10 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11075 | Zone 11 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11076 | Zone 12 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11077 | Zone 13 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11078 | Zone 14 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11079 | Zone 15 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11080 | Zone 16 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11081 | Zone 17 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11082 | Zone 18 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11083 | Zone 19 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11084 | Zone 20 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11085 | Zone 21 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11086 | Zone 22 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11087 | Zone 23 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11088 | Zone 24 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11089 | Zone 25 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11090 | Zone 26 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11091 | Zone 27 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11092 | Zone 28 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11093 | Zone 29 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11094 | Zone 30 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11095 | Zone 31 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11096 | Zone 32 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11097 | Zone 33 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11098 | Zone 34 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11099 | Zone 35 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11100 | Zone 36 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11101 | Zone 37 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11102 | Zone 38 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11103 | Zone 39 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11104 | Zone 40 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11105 | Zone 41 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11106 | Zone 42 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11107 | Zone 43 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11108 | Zone 44 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11109 | Zone 45 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11110 | Zone 46 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11111 | Zone 47 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11112 | Zone 48 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11113 | Zone 49 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11114 | Zone 50 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11115 | Zone 51 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11116 | Zone 52 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11117 | Zone 53 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11118 | Zone 54 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11119 | Zone 55 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11120 | Zone 56 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11121 | Zone 57 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11122 | Zone 58 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11123 | Zone 59 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11124 | Zone 60 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11125 | Zone 61 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11126 | Zone 62 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11127 | Zone 63 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11128 | Zone 64 | Operation Mode | 0 | 4 |  | 0 - Week Calendar, 1 - Forced Manual, 2 - Forced Constant
4:11129 | Zone 1 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11130 | Zone 2 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11131 | Zone 3 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11132 | Zone 4 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11133 | Zone 5 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11134 | Zone 6 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11135 | Zone 7 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11136 | Zone 8 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11137 | Zone 9 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11138 | Zone 10 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11139 | Zone 11 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11140 | Zone 12 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11141 | Zone 13 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11142 | Zone 14 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11143 | Zone 15 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11144 | Zone 16 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11145 | Zone 17 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11146 | Zone 18 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11147 | Zone 19 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11148 | Zone 20 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11149 | Zone 21 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11150 | Zone 22 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11151 | Zone 23 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11152 | Zone 24 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11153 | Zone 25 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11154 | Zone 26 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11155 | Zone 27 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11156 | Zone 28 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11157 | Zone 29 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11158 | Zone 30 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11159 | Zone 31 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11160 | Zone 32 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11161 | Zone 33 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11162 | Zone 34 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11163 | Zone 35 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11164 | Zone 36 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11165 | Zone 37 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11166 | Zone 38 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11167 | Zone 39 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11168 | Zone 40 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11169 | Zone 41 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11170 | Zone 42 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11171 | Zone 43 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11172 | Zone 44 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11173 | Zone 45 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11174 | Zone 46 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11175 | Zone 47 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11176 | Zone 48 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11177 | Zone 49 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11178 | Zone 50 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11179 | Zone 51 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11180 | Zone 52 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11181 | Zone 53 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11182 | Zone 54 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11183 | Zone 55 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11184 | Zone 56 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11185 | Zone 57 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11186 | Zone 58 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11187 | Zone 59 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11188 | Zone 60 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11189 | Zone 61 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11190 | Zone 62 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11191 | Zone 63 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11192 | Zone 64 | User Temp Setpoint | 700 | 4000 | 0,01°C
4:11193 | Zone 1 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11194 | Zone 2 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11195 | Zone 3 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11196 | Zone 4 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11197 | Zone 5 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11198 | Zone 6 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11199 | Zone 7 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11200 | Zone 8 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11201 | Zone 9 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11202 | Zone 10 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11203 | Zone 11 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11204 | Zone 12 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11205 | Zone 13 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11206 | Zone 14 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11207 | Zone 15 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11208 | Zone 16 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11209 | Zone 17 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11210 | Zone 18 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11211 | Zone 19 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11212 | Zone 20 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11213 | Zone 21 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11214 | Zone 22 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11215 | Zone 23 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11216 | Zone 24 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11217 | Zone 25 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11218 | Zone 26 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11219 | Zone 27 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11220 | Zone 28 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11221 | Zone 29 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11222 | Zone 30 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11223 | Zone 31 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11224 | Zone 32 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11225 | Zone 33 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11226 | Zone 34 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11227 | Zone 35 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11228 | Zone 36 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11229 | Zone 37 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11230 | Zone 38 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11231 | Zone 39 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11232 | Zone 40 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11233 | Zone 41 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11234 | Zone 42 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11235 | Zone 43 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11236 | Zone 44 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11237 | Zone 45 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11238 | Zone 46 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11239 | Zone 47 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11240 | Zone 48 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11241 | Zone 49 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11242 | Zone 50 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11243 | Zone 51 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11244 | Zone 52 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11245 | Zone 53 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11246 | Zone 54 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11247 | Zone 55 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11248 | Zone 56 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11249 | Zone 57 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11250 | Zone 58 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11251 | Zone 59 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11252 | Zone 60 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11253 | Zone 61 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11254 | Zone 62 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11255 | Zone 63 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11256 | Zone 64 | Minimum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11257 | Zone 1 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11258 | Zone 2 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11259 | Zone 3 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11260 | Zone 4 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11261 | Zone 5 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11262 | Zone 6 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11263 | Zone 7 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11264 | Zone 8 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11265 | Zone 9 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11266 | Zone 10 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11267 | Zone 11 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11268 | Zone 12 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11269 | Zone 13 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11270 | Zone 14 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11271 | Zone 15 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11272 | Zone 16 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11273 | Zone 17 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11274 | Zone 18 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11275 | Zone 19 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11276 | Zone 20 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11277 | Zone 21 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11278 | Zone 22 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11279 | Zone 23 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11280 | Zone 24 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11281 | Zone 25 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11282 | Zone 26 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11283 | Zone 27 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11284 | Zone 28 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11285 | Zone 29 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11286 | Zone 30 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11287 | Zone 31 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11288 | Zone 32 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11289 | Zone 33 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11290 | Zone 34 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11291 | Zone 35 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11292 | Zone 36 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11293 | Zone 37 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11294 | Zone 38 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11295 | Zone 39 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11296 | Zone 40 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11297 | Zone 41 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11298 | Zone 42 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11299 | Zone 43 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11300 | Zone 44 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11301 | Zone 45 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11302 | Zone 46 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11303 | Zone 47 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11304 | Zone 48 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11305 | Zone 49 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11306 | Zone 50 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11307 | Zone 51 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11308 | Zone 52 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11309 | Zone 53 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11310 | Zone 54 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11311 | Zone 55 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11312 | Zone 56 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11313 | Zone 57 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11314 | Zone 58 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11315 | Zone 59 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11316 | Zone 60 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11317 | Zone 61 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11318 | Zone 62 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11319 | Zone 63 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11320 | Zone 64 | Maximum Temperature Setpoint Restriction | 700 | 4000 | 0,01°C
4:11321 | Zone 1 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11322 | Zone 2 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11323 | Zone 3 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11324 | Zone 4 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11325 | Zone 5 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11326 | Zone 6 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11327 | Zone 7 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11328 | Zone 8 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11329 | Zone 9 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11330 | Zone 10 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11331 | Zone 11 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11332 | Zone 12 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11333 | Zone 13 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11334 | Zone 14 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11335 | Zone 15 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11336 | Zone 16 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11337 | Zone 17 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11338 | Zone 18 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11339 | Zone 19 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11340 | Zone 20 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11341 | Zone 21 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11342 | Zone 22 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11343 | Zone 23 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11344 | Zone 24 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11345 | Zone 25 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11346 | Zone 26 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11347 | Zone 27 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11348 | Zone 28 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11349 | Zone 29 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11350 | Zone 30 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11351 | Zone 31 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11352 | Zone 32 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11353 | Zone 33 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11354 | Zone 34 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11355 | Zone 35 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11356 | Zone 36 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11357 | Zone 37 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11358 | Zone 38 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11359 | Zone 39 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11360 | Zone 40 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11361 | Zone 41 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11362 | Zone 42 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11363 | Zone 43 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11364 | Zone 44 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11365 | Zone 45 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11366 | Zone 46 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11367 | Zone 47 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11368 | Zone 48 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11369 | Zone 49 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11370 | Zone 50 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11371 | Zone 51 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11372 | Zone 52 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11373 | Zone 53 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11374 | Zone 54 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11375 | Zone 55 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11376 | Zone 56 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11377 | Zone 57 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11378 | Zone 58 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11379 | Zone 59 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11380 | Zone 60 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11381 | Zone 61 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11382 | Zone 62 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11383 | Zone 63 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11384 | Zone 64 | Week Program Mode | 0 | 2 |  | 0 - 7-Day Control, 1 - 5/2-Day Control, 2 - 1-Day Control.
4:11385 | Zone 1 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11386 | Zone 2 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11387 | Zone 3 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11388 | Zone 4 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11389 | Zone 5 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11390 | Zone 6 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11391 | Zone 7 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11392 | Zone 8 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11393 | Zone 9 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11394 | Zone 10 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11395 | Zone 11 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11396 | Zone 12 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11397 | Zone 13 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11398 | Zone 14 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11399 | Zone 15 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11400 | Zone 16 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11401 | Zone 17 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11402 | Zone 18 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11403 | Zone 19 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11404 | Zone 20 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11405 | Zone 21 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11406 | Zone 22 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11407 | Zone 23 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11408 | Zone 24 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11409 | Zone 25 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11410 | Zone 26 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11411 | Zone 27 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11412 | Zone 28 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11413 | Zone 29 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11414 | Zone 30 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11415 | Zone 31 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11416 | Zone 32 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11417 | Zone 33 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11418 | Zone 34 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11419 | Zone 35 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11420 | Zone 36 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11421 | Zone 37 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11422 | Zone 38 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11423 | Zone 39 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11424 | Zone 40 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11425 | Zone 41 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11426 | Zone 42 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11427 | Zone 43 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11428 | Zone 44 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11429 | Zone 45 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11430 | Zone 46 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11431 | Zone 47 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11432 | Zone 48 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11433 | Zone 49 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11434 | Zone 50 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11435 | Zone 51 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11436 | Zone 52 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11437 | Zone 53 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11438 | Zone 54 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11439 | Zone 55 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11440 | Zone 56 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11441 | Zone 57 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11442 | Zone 58 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11443 | Zone 59 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11444 | Zone 60 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11445 | Zone 61 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11446 | Zone 62 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11447 | Zone 63 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11448 | Zone 64 | Comfort Temperature Setpoint | 700 | 4000 | 0,01°C
4:11449 | Zone 1 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11450 | Zone 2 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11451 | Zone 3 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11452 | Zone 4 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11453 | Zone 5 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11454 | Zone 6 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11455 | Zone 7 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11456 | Zone 8 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11457 | Zone 9 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11458 | Zone 10 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11459 | Zone 11 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11460 | Zone 12 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11461 | Zone 13 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11462 | Zone 14 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11463 | Zone 15 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11464 | Zone 16 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11465 | Zone 17 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11466 | Zone 18 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11467 | Zone 19 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11468 | Zone 20 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11469 | Zone 21 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11470 | Zone 22 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11471 | Zone 23 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11472 | Zone 24 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11473 | Zone 25 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11474 | Zone 26 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11475 | Zone 27 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11476 | Zone 28 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11477 | Zone 29 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11478 | Zone 30 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11479 | Zone 31 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11480 | Zone 32 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11481 | Zone 33 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11482 | Zone 34 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11483 | Zone 35 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11484 | Zone 36 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11485 | Zone 37 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11486 | Zone 38 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11487 | Zone 39 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11488 | Zone 40 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11489 | Zone 41 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11490 | Zone 42 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11491 | Zone 43 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11492 | Zone 44 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11493 | Zone 45 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11494 | Zone 46 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11495 | Zone 47 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11496 | Zone 48 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11497 | Zone 49 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11498 | Zone 50 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11499 | Zone 51 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11500 | Zone 52 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11501 | Zone 53 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11502 | Zone 54 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11503 | Zone 55 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11504 | Zone 56 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11505 | Zone 57 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11506 | Zone 58 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11507 | Zone 59 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11508 | Zone 60 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11509 | Zone 61 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11510 | Zone 62 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11511 | Zone 63 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11512 | Zone 64 | Economy Temperature Setpoint | 700 | 4000 | 0,01°C
4:11513 | Zone 1 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11514 | Zone 2 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11515 | Zone 3 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11516 | Zone 4 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11517 | Zone 5 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11518 | Zone 6 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11519 | Zone 7 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11520 | Zone 8 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11521 | Zone 9 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11522 | Zone 10 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11523 | Zone 11 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11524 | Zone 12 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11525 | Zone 13 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11526 | Zone 14 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11527 | Zone 15 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11528 | Zone 16 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11529 | Zone 17 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11530 | Zone 18 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11531 | Zone 19 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11532 | Zone 20 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11533 | Zone 21 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11534 | Zone 22 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11535 | Zone 23 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11536 | Zone 24 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11537 | Zone 25 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11538 | Zone 26 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11539 | Zone 27 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11540 | Zone 28 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11541 | Zone 29 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11542 | Zone 30 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11543 | Zone 31 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11544 | Zone 32 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11545 | Zone 33 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11546 | Zone 34 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11547 | Zone 35 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11548 | Zone 36 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11549 | Zone 37 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11550 | Zone 38 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11551 | Zone 39 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11552 | Zone 40 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11553 | Zone 41 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11554 | Zone 42 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11555 | Zone 43 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11556 | Zone 44 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11557 | Zone 45 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11558 | Zone 46 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11559 | Zone 47 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11560 | Zone 48 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11561 | Zone 49 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11562 | Zone 50 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11563 | Zone 51 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11564 | Zone 52 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11565 | Zone 53 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11566 | Zone 54 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11567 | Zone 55 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11568 | Zone 56 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11569 | Zone 57 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11570 | Zone 58 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11571 | Zone 59 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11572 | Zone 60 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11573 | Zone 61 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11574 | Zone 62 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11575 | Zone 63 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11576 | Zone 64 | Setback Temperature Setpoint | 700 | 4000 | 0,01°C
4:11577 | Zone 1 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11578 | Zone 2 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11579 | Zone 3 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11580 | Zone 4 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11581 | Zone 5 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11582 | Zone 6 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11583 | Zone 7 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11584 | Zone 8 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11585 | Zone 9 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11586 | Zone 10 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11587 | Zone 11 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11588 | Zone 12 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11589 | Zone 13 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11590 | Zone 14 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11591 | Zone 15 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11592 | Zone 16 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11593 | Zone 17 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11594 | Zone 18 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11595 | Zone 19 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11596 | Zone 20 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11597 | Zone 21 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11598 | Zone 22 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11599 | Zone 23 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11600 | Zone 24 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11601 | Zone 25 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11602 | Zone 26 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11603 | Zone 27 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11604 | Zone 28 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11605 | Zone 29 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11606 | Zone 30 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11607 | Zone 31 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11608 | Zone 32 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11609 | Zone 33 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11610 | Zone 34 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11611 | Zone 35 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11612 | Zone 36 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11613 | Zone 37 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11614 | Zone 38 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11615 | Zone 39 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11616 | Zone 40 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11617 | Zone 41 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11618 | Zone 42 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11619 | Zone 43 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11620 | Zone 44 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11621 | Zone 45 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11622 | Zone 46 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11623 | Zone 47 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11624 | Zone 48 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11625 | Zone 49 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11626 | Zone 50 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11627 | Zone 51 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11628 | Zone 52 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11629 | Zone 53 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11630 | Zone 54 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11631 | Zone 55 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11632 | Zone 56 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11633 | Zone 57 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11634 | Zone 58 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11635 | Zone 59 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11636 | Zone 60 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11637 | Zone 61 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11638 | Zone 62 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11639 | Zone 63 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11640 | Zone 64 | Holiday Temperature Setpoint | 700 | 4000 | 0,01°C
4:11641 | Zone 1 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11642 | Zone 2 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11643 | Zone 3 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11644 | Zone 4 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11645 | Zone 5 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11646 | Zone 6 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11647 | Zone 7 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11648 | Zone 8 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11649 | Zone 9 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11650 | Zone 10 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11651 | Zone 11 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11652 | Zone 12 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11653 | Zone 13 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11654 | Zone 14 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11655 | Zone 15 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11656 | Zone 16 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11657 | Zone 17 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11658 | Zone 18 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11659 | Zone 19 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11660 | Zone 20 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11661 | Zone 21 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11662 | Zone 22 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11663 | Zone 23 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11664 | Zone 24 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11665 | Zone 25 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11666 | Zone 26 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11667 | Zone 27 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11668 | Zone 28 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11669 | Zone 29 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11670 | Zone 30 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11671 | Zone 31 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11672 | Zone 32 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11673 | Zone 33 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11674 | Zone 34 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11675 | Zone 35 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11676 | Zone 36 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11677 | Zone 37 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11678 | Zone 38 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11679 | Zone 39 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11680 | Zone 40 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11681 | Zone 41 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11682 | Zone 42 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11683 | Zone 43 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11684 | Zone 44 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11685 | Zone 45 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11686 | Zone 46 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11687 | Zone 47 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11688 | Zone 48 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11689 | Zone 49 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11690 | Zone 50 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11691 | Zone 51 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11692 | Zone 52 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11693 | Zone 53 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11694 | Zone 54 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11695 | Zone 55 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11696 | Zone 56 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11697 | Zone 57 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11698 | Zone 58 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11699 | Zone 59 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11700 | Zone 60 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11701 | Zone 61 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11702 | Zone 62 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11703 | Zone 63 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11704 | Zone 64 | Fireplace Compensation Output Min Level | 500 | 10000 | 0,01%
4:11705 | Zone 1 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11706 | Zone 2 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11707 | Zone 3 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11708 | Zone 4 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11709 | Zone 5 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11710 | Zone 6 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11711 | Zone 7 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11712 | Zone 8 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11713 | Zone 9 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11714 | Zone 10 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11715 | Zone 11 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11716 | Zone 12 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11717 | Zone 13 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11718 | Zone 14 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11719 | Zone 15 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11720 | Zone 16 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11721 | Zone 17 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11722 | Zone 18 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11723 | Zone 19 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11724 | Zone 20 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11725 | Zone 21 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11726 | Zone 22 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11727 | Zone 23 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11728 | Zone 24 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11729 | Zone 25 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11730 | Zone 26 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11731 | Zone 27 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11732 | Zone 28 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11733 | Zone 29 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11734 | Zone 30 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11735 | Zone 31 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11736 | Zone 32 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11737 | Zone 33 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11738 | Zone 34 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11739 | Zone 35 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11740 | Zone 36 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11741 | Zone 37 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11742 | Zone 38 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11743 | Zone 39 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11744 | Zone 40 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11745 | Zone 41 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11746 | Zone 42 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11747 | Zone 43 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11748 | Zone 44 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11749 | Zone 45 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11750 | Zone 46 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11751 | Zone 47 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11752 | Zone 48 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11753 | Zone 49 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11754 | Zone 50 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11755 | Zone 51 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11756 | Zone 52 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11757 | Zone 53 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11758 | Zone 54 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11759 | Zone 55 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11760 | Zone 56 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11761 | Zone 57 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11762 | Zone 58 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11763 | Zone 59 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11764 | Zone 60 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11765 | Zone 61 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11766 | Zone 62 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11767 | Zone 63 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11768 | Zone 64 | Bypass Mode | 0 | 2 |  | 0 - By-Pass Function Disabled, 1 - By-Pass Function Enabled. 2 - By-Pass Function "Timed".
4:11769 | Zone 1 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11770 | Zone 2 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11771 | Zone 3 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11772 | Zone 4 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11773 | Zone 5 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11774 | Zone 6 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11775 | Zone 7 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11776 | Zone 8 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11777 | Zone 9 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11778 | Zone 10 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11779 | Zone 11 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11780 | Zone 12 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11781 | Zone 13 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11782 | Zone 14 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11783 | Zone 15 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11784 | Zone 16 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11785 | Zone 17 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11786 | Zone 18 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11787 | Zone 19 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11788 | Zone 20 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11789 | Zone 21 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11790 | Zone 22 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11791 | Zone 23 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11792 | Zone 24 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11793 | Zone 25 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11794 | Zone 26 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11795 | Zone 27 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11796 | Zone 28 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11797 | Zone 29 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11798 | Zone 30 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11799 | Zone 31 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11800 | Zone 32 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11801 | Zone 33 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11802 | Zone 34 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11803 | Zone 35 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11804 | Zone 36 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11805 | Zone 37 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11806 | Zone 38 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11807 | Zone 39 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11808 | Zone 40 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11809 | Zone 41 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11810 | Zone 42 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11811 | Zone 43 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11812 | Zone 44 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11813 | Zone 45 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11814 | Zone 46 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11815 | Zone 47 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11816 | Zone 48 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11817 | Zone 49 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11818 | Zone 50 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11819 | Zone 51 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11820 | Zone 52 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11821 | Zone 53 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11822 | Zone 54 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11823 | Zone 55 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11824 | Zone 56 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11825 | Zone 57 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11826 | Zone 58 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11827 | Zone 59 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11828 | Zone 60 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11829 | Zone 61 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11830 | Zone 62 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11831 | Zone 63 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11832 | Zone 64 | Sensor Mode | 0 | 3 |  | 0 - Room, 1 - Floor, 2 - Room + Min Floor, 3 - Room + Max Floor
4:11833 | Zone 1 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11834 | Zone 2 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11835 | Zone 3 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11836 | Zone 4 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11837 | Zone 5 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11838 | Zone 6 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11839 | Zone 7 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11840 | Zone 8 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11841 | Zone 9 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11842 | Zone 10 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11843 | Zone 11 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11844 | Zone 12 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11845 | Zone 13 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11846 | Zone 14 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11847 | Zone 15 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11848 | Zone 16 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11849 | Zone 17 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11850 | Zone 18 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11851 | Zone 19 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11852 | Zone 20 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11853 | Zone 21 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11854 | Zone 22 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11855 | Zone 23 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11856 | Zone 24 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11857 | Zone 25 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11858 | Zone 26 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11859 | Zone 27 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11860 | Zone 28 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11861 | Zone 29 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11862 | Zone 30 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11863 | Zone 31 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11864 | Zone 32 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11865 | Zone 33 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11866 | Zone 34 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11867 | Zone 35 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11868 | Zone 36 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11869 | Zone 37 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11870 | Zone 38 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11871 | Zone 39 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11872 | Zone 40 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11873 | Zone 41 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11874 | Zone 42 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11875 | Zone 43 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11876 | Zone 44 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11877 | Zone 45 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11878 | Zone 46 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11879 | Zone 47 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11880 | Zone 48 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11881 | Zone 49 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11882 | Zone 50 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11883 | Zone 51 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11884 | Zone 52 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11885 | Zone 53 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11886 | Zone 54 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11887 | Zone 55 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11888 | Zone 56 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11889 | Zone 57 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11890 | Zone 58 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11891 | Zone 59 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11892 | Zone 60 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11893 | Zone 61 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11894 | Zone 62 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11895 | Zone 63 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11896 | Zone 64 | Floor Temp Min Limit | 700 | 4000 | 0,01°C
4:11897 | Zone 1 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11898 | Zone 2 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11899 | Zone 3 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11900 | Zone 4 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11901 | Zone 5 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11902 | Zone 6 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11903 | Zone 7 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11904 | Zone 8 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11905 | Zone 9 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11906 | Zone 10 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11907 | Zone 11 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11908 | Zone 12 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11909 | Zone 13 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11910 | Zone 14 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11911 | Zone 15 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11912 | Zone 16 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11913 | Zone 17 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11914 | Zone 18 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11915 | Zone 19 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11916 | Zone 20 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11917 | Zone 21 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11918 | Zone 22 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11919 | Zone 23 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11920 | Zone 24 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11921 | Zone 25 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11922 | Zone 26 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11923 | Zone 27 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11924 | Zone 28 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11925 | Zone 29 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11926 | Zone 30 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11927 | Zone 31 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11928 | Zone 32 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11929 | Zone 33 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11930 | Zone 34 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11931 | Zone 35 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11932 | Zone 36 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11933 | Zone 37 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11934 | Zone 38 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11935 | Zone 39 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11936 | Zone 40 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11937 | Zone 41 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11938 | Zone 42 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11939 | Zone 43 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11940 | Zone 44 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11941 | Zone 45 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11942 | Zone 46 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11943 | Zone 47 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11944 | Zone 48 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11945 | Zone 49 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11946 | Zone 50 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11947 | Zone 51 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11948 | Zone 52 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11949 | Zone 53 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11950 | Zone 54 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11951 | Zone 55 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11952 | Zone 56 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11953 | Zone 57 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11954 | Zone 58 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11955 | Zone 59 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11956 | Zone 60 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11957 | Zone 61 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11958 | Zone 62 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11959 | Zone 63 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11960 | Zone 64 | Floor Temp Max Limit | 700 | 4000 | 0,01°C
4:11961 | Zone 1 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11962 | Zone 2 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11963 | Zone 3 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11964 | Zone 4 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11965 | Zone 5 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11966 | Zone 6 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11967 | Zone 7 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11968 | Zone 8 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11969 | Zone 9 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11970 | Zone 10 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11971 | Zone 11 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11972 | Zone 12 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11973 | Zone 13 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11974 | Zone 14 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11975 | Zone 15 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11976 | Zone 16 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11977 | Zone 17 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11978 | Zone 18 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11979 | Zone 19 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11980 | Zone 20 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11981 | Zone 21 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11982 | Zone 22 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11983 | Zone 23 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11984 | Zone 24 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11985 | Zone 25 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11986 | Zone 26 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11987 | Zone 27 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11988 | Zone 28 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11989 | Zone 29 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11990 | Zone 30 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11991 | Zone 31 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11992 | Zone 32 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11993 | Zone 33 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11994 | Zone 34 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11995 | Zone 35 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11996 | Zone 36 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11997 | Zone 37 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11998 | Zone 38 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:11999 | Zone 39 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12000 | Zone 40 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12001 | Zone 41 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12002 | Zone 42 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12003 | Zone 43 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12004 | Zone 44 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12005 | Zone 45 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12006 | Zone 46 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12007 | Zone 47 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12008 | Zone 48 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12009 | Zone 49 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12010 | Zone 50 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12011 | Zone 51 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12012 | Zone 52 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12013 | Zone 53 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12014 | Zone 54 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12015 | Zone 55 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12016 | Zone 56 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12017 | Zone 57 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12018 | Zone 58 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12019 | Zone 59 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12020 | Zone 60 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12021 | Zone 61 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12022 | Zone 62 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12023 | Zone 63 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12024 | Zone 64 | Day 1 Event 1 Start Time | 0 | 1440 | min
4:12025 | Zone 1 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12026 | Zone 2 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12027 | Zone 3 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12028 | Zone 4 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12029 | Zone 5 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12030 | Zone 6 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12031 | Zone 7 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12032 | Zone 8 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12033 | Zone 9 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12034 | Zone 10 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12035 | Zone 11 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12036 | Zone 12 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12037 | Zone 13 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12038 | Zone 14 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12039 | Zone 15 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12040 | Zone 16 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12041 | Zone 17 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12042 | Zone 18 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12043 | Zone 19 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12044 | Zone 20 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12045 | Zone 21 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12046 | Zone 22 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12047 | Zone 23 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12048 | Zone 24 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12049 | Zone 25 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12050 | Zone 26 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12051 | Zone 27 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12052 | Zone 28 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12053 | Zone 29 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12054 | Zone 30 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12055 | Zone 31 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12056 | Zone 32 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12057 | Zone 33 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12058 | Zone 34 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12059 | Zone 35 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12060 | Zone 36 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12061 | Zone 37 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12062 | Zone 38 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12063 | Zone 39 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12064 | Zone 40 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12065 | Zone 41 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12066 | Zone 42 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12067 | Zone 43 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12068 | Zone 44 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12069 | Zone 45 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12070 | Zone 46 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12071 | Zone 47 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12072 | Zone 48 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12073 | Zone 49 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12074 | Zone 50 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12075 | Zone 51 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12076 | Zone 52 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12077 | Zone 53 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12078 | Zone 54 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12079 | Zone 55 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12080 | Zone 56 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12081 | Zone 57 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12082 | Zone 58 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12083 | Zone 59 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12084 | Zone 60 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12085 | Zone 61 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12086 | Zone 62 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12087 | Zone 63 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12088 | Zone 64 | Day 1 Event 1 End Time | 0 | 1440 | min
4:12089 | Zone 1 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12090 | Zone 2 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12091 | Zone 3 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12092 | Zone 4 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12093 | Zone 5 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12094 | Zone 6 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12095 | Zone 7 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12096 | Zone 8 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12097 | Zone 9 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12098 | Zone 10 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12099 | Zone 11 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12100 | Zone 12 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12101 | Zone 13 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12102 | Zone 14 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12103 | Zone 15 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12104 | Zone 16 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12105 | Zone 17 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12106 | Zone 18 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12107 | Zone 19 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12108 | Zone 20 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12109 | Zone 21 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12110 | Zone 22 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12111 | Zone 23 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12112 | Zone 24 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12113 | Zone 25 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12114 | Zone 26 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12115 | Zone 27 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12116 | Zone 28 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12117 | Zone 29 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12118 | Zone 30 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12119 | Zone 31 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12120 | Zone 32 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12121 | Zone 33 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12122 | Zone 34 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12123 | Zone 35 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12124 | Zone 36 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12125 | Zone 37 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12126 | Zone 38 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12127 | Zone 39 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12128 | Zone 40 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12129 | Zone 41 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12130 | Zone 42 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12131 | Zone 43 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12132 | Zone 44 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12133 | Zone 45 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12134 | Zone 46 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12135 | Zone 47 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12136 | Zone 48 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12137 | Zone 49 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12138 | Zone 50 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12139 | Zone 51 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12140 | Zone 52 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12141 | Zone 53 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12142 | Zone 54 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12143 | Zone 55 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12144 | Zone 56 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12145 | Zone 57 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12146 | Zone 58 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12147 | Zone 59 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12148 | Zone 60 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12149 | Zone 61 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12150 | Zone 62 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12151 | Zone 63 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12152 | Zone 64 | Day 1 Event 2 Start Time | 0 | 1440 | min
4:12153 | Zone 1 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12154 | Zone 2 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12155 | Zone 3 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12156 | Zone 4 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12157 | Zone 5 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12158 | Zone 6 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12159 | Zone 7 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12160 | Zone 8 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12161 | Zone 9 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12162 | Zone 10 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12163 | Zone 11 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12164 | Zone 12 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12165 | Zone 13 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12166 | Zone 14 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12167 | Zone 15 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12168 | Zone 16 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12169 | Zone 17 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12170 | Zone 18 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12171 | Zone 19 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12172 | Zone 20 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12173 | Zone 21 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12174 | Zone 22 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12175 | Zone 23 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12176 | Zone 24 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12177 | Zone 25 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12178 | Zone 26 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12179 | Zone 27 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12180 | Zone 28 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12181 | Zone 29 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12182 | Zone 30 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12183 | Zone 31 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12184 | Zone 32 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12185 | Zone 33 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12186 | Zone 34 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12187 | Zone 35 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12188 | Zone 36 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12189 | Zone 37 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12190 | Zone 38 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12191 | Zone 39 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12192 | Zone 40 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12193 | Zone 41 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12194 | Zone 42 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12195 | Zone 43 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12196 | Zone 44 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12197 | Zone 45 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12198 | Zone 46 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12199 | Zone 47 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12200 | Zone 48 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12201 | Zone 49 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12202 | Zone 50 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12203 | Zone 51 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12204 | Zone 52 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12205 | Zone 53 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12206 | Zone 54 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12207 | Zone 55 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12208 | Zone 56 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12209 | Zone 57 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12210 | Zone 58 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12211 | Zone 59 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12212 | Zone 60 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12213 | Zone 61 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12214 | Zone 62 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12215 | Zone 63 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12216 | Zone 64 | Day 1 Event 2 End Time | 0 | 1440 | min
4:12217 | Zone 1 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12218 | Zone 2 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12219 | Zone 3 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12220 | Zone 4 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12221 | Zone 5 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12222 | Zone 6 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12223 | Zone 7 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12224 | Zone 8 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12225 | Zone 9 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12226 | Zone 10 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12227 | Zone 11 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12228 | Zone 12 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12229 | Zone 13 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12230 | Zone 14 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12231 | Zone 15 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12232 | Zone 16 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12233 | Zone 17 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12234 | Zone 18 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12235 | Zone 19 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12236 | Zone 20 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12237 | Zone 21 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12238 | Zone 22 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12239 | Zone 23 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12240 | Zone 24 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12241 | Zone 25 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12242 | Zone 26 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12243 | Zone 27 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12244 | Zone 28 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12245 | Zone 29 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12246 | Zone 30 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12247 | Zone 31 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12248 | Zone 32 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12249 | Zone 33 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12250 | Zone 34 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12251 | Zone 35 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12252 | Zone 36 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12253 | Zone 37 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12254 | Zone 38 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12255 | Zone 39 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12256 | Zone 40 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12257 | Zone 41 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12258 | Zone 42 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12259 | Zone 43 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12260 | Zone 44 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12261 | Zone 45 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12262 | Zone 46 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12263 | Zone 47 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12264 | Zone 48 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12265 | Zone 49 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12266 | Zone 50 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12267 | Zone 51 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12268 | Zone 52 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12269 | Zone 53 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12270 | Zone 54 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12271 | Zone 55 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12272 | Zone 56 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12273 | Zone 57 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12274 | Zone 58 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12275 | Zone 59 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12276 | Zone 60 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12277 | Zone 61 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12278 | Zone 62 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12279 | Zone 63 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12280 | Zone 64 | Day 1 Event 3 Start Time | 0 | 1440 | min
4:12281 | Zone 1 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12282 | Zone 2 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12283 | Zone 3 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12284 | Zone 4 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12285 | Zone 5 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12286 | Zone 6 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12287 | Zone 7 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12288 | Zone 8 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12289 | Zone 9 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12290 | Zone 10 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12291 | Zone 11 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12292 | Zone 12 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12293 | Zone 13 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12294 | Zone 14 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12295 | Zone 15 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12296 | Zone 16 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12297 | Zone 17 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12298 | Zone 18 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12299 | Zone 19 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12300 | Zone 20 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12301 | Zone 21 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12302 | Zone 22 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12303 | Zone 23 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12304 | Zone 24 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12305 | Zone 25 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12306 | Zone 26 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12307 | Zone 27 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12308 | Zone 28 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12309 | Zone 29 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12310 | Zone 30 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12311 | Zone 31 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12312 | Zone 32 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12313 | Zone 33 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12314 | Zone 34 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12315 | Zone 35 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12316 | Zone 36 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12317 | Zone 37 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12318 | Zone 38 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12319 | Zone 39 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12320 | Zone 40 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12321 | Zone 41 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12322 | Zone 42 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12323 | Zone 43 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12324 | Zone 44 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12325 | Zone 45 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12326 | Zone 46 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12327 | Zone 47 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12328 | Zone 48 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12329 | Zone 49 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12330 | Zone 50 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12331 | Zone 51 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12332 | Zone 52 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12333 | Zone 53 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12334 | Zone 54 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12335 | Zone 55 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12336 | Zone 56 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12337 | Zone 57 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12338 | Zone 58 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12339 | Zone 59 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12340 | Zone 60 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12341 | Zone 61 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12342 | Zone 62 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12343 | Zone 63 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12344 | Zone 64 | Day 1 Event 3 End Time | 0 | 1440 | min
4:12345 | Zone 1 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12346 | Zone 2 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12347 | Zone 3 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12348 | Zone 4 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12349 | Zone 5 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12350 | Zone 6 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12351 | Zone 7 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12352 | Zone 8 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12353 | Zone 9 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12354 | Zone 10 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12355 | Zone 11 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12356 | Zone 12 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12357 | Zone 13 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12358 | Zone 14 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12359 | Zone 15 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12360 | Zone 16 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12361 | Zone 17 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12362 | Zone 18 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12363 | Zone 19 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12364 | Zone 20 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12365 | Zone 21 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12366 | Zone 22 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12367 | Zone 23 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12368 | Zone 24 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12369 | Zone 25 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12370 | Zone 26 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12371 | Zone 27 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12372 | Zone 28 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12373 | Zone 29 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12374 | Zone 30 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12375 | Zone 31 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12376 | Zone 32 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12377 | Zone 33 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12378 | Zone 34 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12379 | Zone 35 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12380 | Zone 36 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12381 | Zone 37 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12382 | Zone 38 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12383 | Zone 39 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12384 | Zone 40 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12385 | Zone 41 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12386 | Zone 42 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12387 | Zone 43 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12388 | Zone 44 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12389 | Zone 45 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12390 | Zone 46 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12391 | Zone 47 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12392 | Zone 48 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12393 | Zone 49 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12394 | Zone 50 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12395 | Zone 51 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12396 | Zone 52 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12397 | Zone 53 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12398 | Zone 54 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12399 | Zone 55 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12400 | Zone 56 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12401 | Zone 57 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12402 | Zone 58 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12403 | Zone 59 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12404 | Zone 60 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12405 | Zone 61 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12406 | Zone 62 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12407 | Zone 63 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12408 | Zone 64 | Day 2 Event 1 Start Time | 0 | 1440 | min
4:12409 | Zone 1 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12410 | Zone 2 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12411 | Zone 3 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12412 | Zone 4 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12413 | Zone 5 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12414 | Zone 6 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12415 | Zone 7 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12416 | Zone 8 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12417 | Zone 9 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12418 | Zone 10 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12419 | Zone 11 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12420 | Zone 12 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12421 | Zone 13 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12422 | Zone 14 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12423 | Zone 15 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12424 | Zone 16 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12425 | Zone 17 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12426 | Zone 18 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12427 | Zone 19 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12428 | Zone 20 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12429 | Zone 21 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12430 | Zone 22 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12431 | Zone 23 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12432 | Zone 24 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12433 | Zone 25 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12434 | Zone 26 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12435 | Zone 27 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12436 | Zone 28 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12437 | Zone 29 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12438 | Zone 30 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12439 | Zone 31 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12440 | Zone 32 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12441 | Zone 33 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12442 | Zone 34 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12443 | Zone 35 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12444 | Zone 36 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12445 | Zone 37 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12446 | Zone 38 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12447 | Zone 39 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12448 | Zone 40 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12449 | Zone 41 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12450 | Zone 42 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12451 | Zone 43 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12452 | Zone 44 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12453 | Zone 45 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12454 | Zone 46 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12455 | Zone 47 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12456 | Zone 48 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12457 | Zone 49 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12458 | Zone 50 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12459 | Zone 51 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12460 | Zone 52 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12461 | Zone 53 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12462 | Zone 54 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12463 | Zone 55 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12464 | Zone 56 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12465 | Zone 57 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12466 | Zone 58 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12467 | Zone 59 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12468 | Zone 60 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12469 | Zone 61 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12470 | Zone 62 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12471 | Zone 63 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12472 | Zone 64 | Day 2 Event 1 End Time | 0 | 1440 | min
4:12473 | Zone 1 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12474 | Zone 2 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12475 | Zone 3 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12476 | Zone 4 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12477 | Zone 5 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12478 | Zone 6 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12479 | Zone 7 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12480 | Zone 8 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12481 | Zone 9 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12482 | Zone 10 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12483 | Zone 11 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12484 | Zone 12 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12485 | Zone 13 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12486 | Zone 14 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12487 | Zone 15 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12488 | Zone 16 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12489 | Zone 17 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12490 | Zone 18 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12491 | Zone 19 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12492 | Zone 20 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12493 | Zone 21 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12494 | Zone 22 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12495 | Zone 23 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12496 | Zone 24 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12497 | Zone 25 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12498 | Zone 26 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12499 | Zone 27 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12500 | Zone 28 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12501 | Zone 29 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12502 | Zone 30 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12503 | Zone 31 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12504 | Zone 32 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12505 | Zone 33 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12506 | Zone 34 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12507 | Zone 35 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12508 | Zone 36 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12509 | Zone 37 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12510 | Zone 38 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12511 | Zone 39 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12512 | Zone 40 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12513 | Zone 41 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12514 | Zone 42 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12515 | Zone 43 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12516 | Zone 44 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12517 | Zone 45 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12518 | Zone 46 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12519 | Zone 47 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12520 | Zone 48 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12521 | Zone 49 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12522 | Zone 50 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12523 | Zone 51 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12524 | Zone 52 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12525 | Zone 53 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12526 | Zone 54 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12527 | Zone 55 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12528 | Zone 56 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12529 | Zone 57 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12530 | Zone 58 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12531 | Zone 59 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12532 | Zone 60 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12533 | Zone 61 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12534 | Zone 62 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12535 | Zone 63 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12536 | Zone 64 | Day 2 Event 2 Start Time | 0 | 1440 | min
4:12537 | Zone 1 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12538 | Zone 2 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12539 | Zone 3 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12540 | Zone 4 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12541 | Zone 5 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12542 | Zone 6 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12543 | Zone 7 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12544 | Zone 8 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12545 | Zone 9 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12546 | Zone 10 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12547 | Zone 11 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12548 | Zone 12 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12549 | Zone 13 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12550 | Zone 14 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12551 | Zone 15 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12552 | Zone 16 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12553 | Zone 17 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12554 | Zone 18 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12555 | Zone 19 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12556 | Zone 20 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12557 | Zone 21 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12558 | Zone 22 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12559 | Zone 23 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12560 | Zone 24 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12561 | Zone 25 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12562 | Zone 26 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12563 | Zone 27 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12564 | Zone 28 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12565 | Zone 29 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12566 | Zone 30 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12567 | Zone 31 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12568 | Zone 32 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12569 | Zone 33 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12570 | Zone 34 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12571 | Zone 35 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12572 | Zone 36 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12573 | Zone 37 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12574 | Zone 38 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12575 | Zone 39 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12576 | Zone 40 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12577 | Zone 41 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12578 | Zone 42 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12579 | Zone 43 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12580 | Zone 44 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12581 | Zone 45 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12582 | Zone 46 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12583 | Zone 47 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12584 | Zone 48 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12585 | Zone 49 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12586 | Zone 50 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12587 | Zone 51 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12588 | Zone 52 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12589 | Zone 53 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12590 | Zone 54 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12591 | Zone 55 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12592 | Zone 56 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12593 | Zone 57 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12594 | Zone 58 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12595 | Zone 59 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12596 | Zone 60 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12597 | Zone 61 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12598 | Zone 62 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12599 | Zone 63 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12600 | Zone 64 | Day 2 Event 2 End Time | 0 | 1440 | min
4:12601 | Zone 1 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12602 | Zone 2 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12603 | Zone 3 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12604 | Zone 4 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12605 | Zone 5 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12606 | Zone 6 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12607 | Zone 7 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12608 | Zone 8 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12609 | Zone 9 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12610 | Zone 10 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12611 | Zone 11 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12612 | Zone 12 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12613 | Zone 13 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12614 | Zone 14 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12615 | Zone 15 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12616 | Zone 16 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12617 | Zone 17 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12618 | Zone 18 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12619 | Zone 19 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12620 | Zone 20 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12621 | Zone 21 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12622 | Zone 22 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12623 | Zone 23 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12624 | Zone 24 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12625 | Zone 25 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12626 | Zone 26 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12627 | Zone 27 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12628 | Zone 28 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12629 | Zone 29 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12630 | Zone 30 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12631 | Zone 31 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12632 | Zone 32 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12633 | Zone 33 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12634 | Zone 34 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12635 | Zone 35 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12636 | Zone 36 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12637 | Zone 37 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12638 | Zone 38 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12639 | Zone 39 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12640 | Zone 40 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12641 | Zone 41 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12642 | Zone 42 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12643 | Zone 43 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12644 | Zone 44 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12645 | Zone 45 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12646 | Zone 46 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12647 | Zone 47 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12648 | Zone 48 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12649 | Zone 49 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12650 | Zone 50 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12651 | Zone 51 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12652 | Zone 52 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12653 | Zone 53 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12654 | Zone 54 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12655 | Zone 55 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12656 | Zone 56 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12657 | Zone 57 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12658 | Zone 58 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12659 | Zone 59 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12660 | Zone 60 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12661 | Zone 61 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12662 | Zone 62 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12663 | Zone 63 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12664 | Zone 64 | Day 2 Event 3 Start Time | 0 | 1440 | min
4:12665 | Zone 1 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12666 | Zone 2 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12667 | Zone 3 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12668 | Zone 4 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12669 | Zone 5 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12670 | Zone 6 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12671 | Zone 7 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12672 | Zone 8 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12673 | Zone 9 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12674 | Zone 10 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12675 | Zone 11 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12676 | Zone 12 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12677 | Zone 13 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12678 | Zone 14 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12679 | Zone 15 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12680 | Zone 16 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12681 | Zone 17 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12682 | Zone 18 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12683 | Zone 19 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12684 | Zone 20 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12685 | Zone 21 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12686 | Zone 22 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12687 | Zone 23 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12688 | Zone 24 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12689 | Zone 25 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12690 | Zone 26 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12691 | Zone 27 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12692 | Zone 28 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12693 | Zone 29 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12694 | Zone 30 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12695 | Zone 31 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12696 | Zone 32 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12697 | Zone 33 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12698 | Zone 34 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12699 | Zone 35 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12700 | Zone 36 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12701 | Zone 37 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12702 | Zone 38 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12703 | Zone 39 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12704 | Zone 40 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12705 | Zone 41 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12706 | Zone 42 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12707 | Zone 43 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12708 | Zone 44 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12709 | Zone 45 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12710 | Zone 46 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12711 | Zone 47 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12712 | Zone 48 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12713 | Zone 49 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12714 | Zone 50 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12715 | Zone 51 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12716 | Zone 52 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12717 | Zone 53 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12718 | Zone 54 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12719 | Zone 55 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12720 | Zone 56 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12721 | Zone 57 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12722 | Zone 58 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12723 | Zone 59 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12724 | Zone 60 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12725 | Zone 61 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12726 | Zone 62 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12727 | Zone 63 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12728 | Zone 64 | Day 2 Event 3 End Time | 0 | 1440 | min
4:12729 | Zone 1 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12730 | Zone 2 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12731 | Zone 3 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12732 | Zone 4 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12733 | Zone 5 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12734 | Zone 6 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12735 | Zone 7 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12736 | Zone 8 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12737 | Zone 9 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12738 | Zone 10 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12739 | Zone 11 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12740 | Zone 12 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12741 | Zone 13 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12742 | Zone 14 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12743 | Zone 15 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12744 | Zone 16 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12745 | Zone 17 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12746 | Zone 18 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12747 | Zone 19 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12748 | Zone 20 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12749 | Zone 21 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12750 | Zone 22 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12751 | Zone 23 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12752 | Zone 24 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12753 | Zone 25 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12754 | Zone 26 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12755 | Zone 27 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12756 | Zone 28 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12757 | Zone 29 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12758 | Zone 30 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12759 | Zone 31 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12760 | Zone 32 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12761 | Zone 33 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12762 | Zone 34 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12763 | Zone 35 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12764 | Zone 36 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12765 | Zone 37 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12766 | Zone 38 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12767 | Zone 39 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12768 | Zone 40 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12769 | Zone 41 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12770 | Zone 42 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12771 | Zone 43 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12772 | Zone 44 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12773 | Zone 45 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12774 | Zone 46 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12775 | Zone 47 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12776 | Zone 48 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12777 | Zone 49 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12778 | Zone 50 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12779 | Zone 51 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12780 | Zone 52 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12781 | Zone 53 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12782 | Zone 54 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12783 | Zone 55 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12784 | Zone 56 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12785 | Zone 57 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12786 | Zone 58 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12787 | Zone 59 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12788 | Zone 60 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12789 | Zone 61 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12790 | Zone 62 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12791 | Zone 63 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12792 | Zone 64 | Day 3 Event 1 Start Time | 0 | 1440 | min
4:12793 | Zone 1 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12794 | Zone 2 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12795 | Zone 3 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12796 | Zone 4 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12797 | Zone 5 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12798 | Zone 6 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12799 | Zone 7 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12800 | Zone 8 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12801 | Zone 9 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12802 | Zone 10 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12803 | Zone 11 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12804 | Zone 12 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12805 | Zone 13 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12806 | Zone 14 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12807 | Zone 15 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12808 | Zone 16 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12809 | Zone 17 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12810 | Zone 18 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12811 | Zone 19 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12812 | Zone 20 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12813 | Zone 21 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12814 | Zone 22 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12815 | Zone 23 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12816 | Zone 24 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12817 | Zone 25 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12818 | Zone 26 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12819 | Zone 27 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12820 | Zone 28 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12821 | Zone 29 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12822 | Zone 30 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12823 | Zone 31 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12824 | Zone 32 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12825 | Zone 33 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12826 | Zone 34 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12827 | Zone 35 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12828 | Zone 36 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12829 | Zone 37 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12830 | Zone 38 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12831 | Zone 39 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12832 | Zone 40 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12833 | Zone 41 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12834 | Zone 42 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12835 | Zone 43 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12836 | Zone 44 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12837 | Zone 45 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12838 | Zone 46 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12839 | Zone 47 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12840 | Zone 48 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12841 | Zone 49 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12842 | Zone 50 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12843 | Zone 51 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12844 | Zone 52 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12845 | Zone 53 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12846 | Zone 54 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12847 | Zone 55 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12848 | Zone 56 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12849 | Zone 57 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12850 | Zone 58 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12851 | Zone 59 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12852 | Zone 60 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12853 | Zone 61 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12854 | Zone 62 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12855 | Zone 63 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12856 | Zone 64 | Day 3 Event 1 End Time | 0 | 1440 | min
4:12857 | Zone 1 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12858 | Zone 2 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12859 | Zone 3 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12860 | Zone 4 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12861 | Zone 5 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12862 | Zone 6 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12863 | Zone 7 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12864 | Zone 8 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12865 | Zone 9 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12866 | Zone 10 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12867 | Zone 11 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12868 | Zone 12 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12869 | Zone 13 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12870 | Zone 14 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12871 | Zone 15 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12872 | Zone 16 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12873 | Zone 17 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12874 | Zone 18 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12875 | Zone 19 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12876 | Zone 20 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12877 | Zone 21 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12878 | Zone 22 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12879 | Zone 23 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12880 | Zone 24 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12881 | Zone 25 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12882 | Zone 26 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12883 | Zone 27 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12884 | Zone 28 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12885 | Zone 29 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12886 | Zone 30 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12887 | Zone 31 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12888 | Zone 32 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12889 | Zone 33 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12890 | Zone 34 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12891 | Zone 35 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12892 | Zone 36 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12893 | Zone 37 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12894 | Zone 38 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12895 | Zone 39 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12896 | Zone 40 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12897 | Zone 41 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12898 | Zone 42 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12899 | Zone 43 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12900 | Zone 44 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12901 | Zone 45 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12902 | Zone 46 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12903 | Zone 47 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12904 | Zone 48 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12905 | Zone 49 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12906 | Zone 50 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12907 | Zone 51 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12908 | Zone 52 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12909 | Zone 53 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12910 | Zone 54 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12911 | Zone 55 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12912 | Zone 56 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12913 | Zone 57 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12914 | Zone 58 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12915 | Zone 59 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12916 | Zone 60 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12917 | Zone 61 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12918 | Zone 62 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12919 | Zone 63 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12920 | Zone 64 | Day 3 Event 2 Start Time | 0 | 1440 | min
4:12921 | Zone 1 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12922 | Zone 2 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12923 | Zone 3 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12924 | Zone 4 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12925 | Zone 5 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12926 | Zone 6 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12927 | Zone 7 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12928 | Zone 8 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12929 | Zone 9 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12930 | Zone 10 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12931 | Zone 11 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12932 | Zone 12 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12933 | Zone 13 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12934 | Zone 14 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12935 | Zone 15 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12936 | Zone 16 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12937 | Zone 17 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12938 | Zone 18 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12939 | Zone 19 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12940 | Zone 20 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12941 | Zone 21 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12942 | Zone 22 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12943 | Zone 23 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12944 | Zone 24 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12945 | Zone 25 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12946 | Zone 26 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12947 | Zone 27 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12948 | Zone 28 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12949 | Zone 29 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12950 | Zone 30 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12951 | Zone 31 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12952 | Zone 32 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12953 | Zone 33 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12954 | Zone 34 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12955 | Zone 35 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12956 | Zone 36 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12957 | Zone 37 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12958 | Zone 38 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12959 | Zone 39 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12960 | Zone 40 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12961 | Zone 41 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12962 | Zone 42 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12963 | Zone 43 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12964 | Zone 44 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12965 | Zone 45 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12966 | Zone 46 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12967 | Zone 47 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12968 | Zone 48 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12969 | Zone 49 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12970 | Zone 50 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12971 | Zone 51 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12972 | Zone 52 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12973 | Zone 53 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12974 | Zone 54 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12975 | Zone 55 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12976 | Zone 56 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12977 | Zone 57 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12978 | Zone 58 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12979 | Zone 59 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12980 | Zone 60 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12981 | Zone 61 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12982 | Zone 62 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12983 | Zone 63 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12984 | Zone 64 | Day 3 Event 2 End Time | 0 | 1440 | min
4:12985 | Zone 1 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12986 | Zone 2 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12987 | Zone 3 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12988 | Zone 4 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12989 | Zone 5 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12990 | Zone 6 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12991 | Zone 7 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12992 | Zone 8 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12993 | Zone 9 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12994 | Zone 10 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12995 | Zone 11 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12996 | Zone 12 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12997 | Zone 13 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12998 | Zone 14 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:12999 | Zone 15 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13000 | Zone 16 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13001 | Zone 17 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13002 | Zone 18 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13003 | Zone 19 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13004 | Zone 20 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13005 | Zone 21 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13006 | Zone 22 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13007 | Zone 23 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13008 | Zone 24 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13009 | Zone 25 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13010 | Zone 26 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13011 | Zone 27 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13012 | Zone 28 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13013 | Zone 29 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13014 | Zone 30 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13015 | Zone 31 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13016 | Zone 32 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13017 | Zone 33 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13018 | Zone 34 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13019 | Zone 35 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13020 | Zone 36 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13021 | Zone 37 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13022 | Zone 38 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13023 | Zone 39 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13024 | Zone 40 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13025 | Zone 41 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13026 | Zone 42 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13027 | Zone 43 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13028 | Zone 44 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13029 | Zone 45 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13030 | Zone 46 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13031 | Zone 47 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13032 | Zone 48 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13033 | Zone 49 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13034 | Zone 50 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13035 | Zone 51 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13036 | Zone 52 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13037 | Zone 53 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13038 | Zone 54 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13039 | Zone 55 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13040 | Zone 56 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13041 | Zone 57 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13042 | Zone 58 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13043 | Zone 59 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13044 | Zone 60 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13045 | Zone 61 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13046 | Zone 62 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13047 | Zone 63 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13048 | Zone 64 | Day 3 Event 3 Start Time | 0 | 1440 | min
4:13049 | Zone 1 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13050 | Zone 2 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13051 | Zone 3 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13052 | Zone 4 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13053 | Zone 5 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13054 | Zone 6 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13055 | Zone 7 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13056 | Zone 8 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13057 | Zone 9 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13058 | Zone 10 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13059 | Zone 11 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13060 | Zone 12 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13061 | Zone 13 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13062 | Zone 14 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13063 | Zone 15 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13064 | Zone 16 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13065 | Zone 17 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13066 | Zone 18 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13067 | Zone 19 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13068 | Zone 20 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13069 | Zone 21 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13070 | Zone 22 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13071 | Zone 23 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13072 | Zone 24 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13073 | Zone 25 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13074 | Zone 26 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13075 | Zone 27 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13076 | Zone 28 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13077 | Zone 29 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13078 | Zone 30 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13079 | Zone 31 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13080 | Zone 32 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13081 | Zone 33 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13082 | Zone 34 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13083 | Zone 35 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13084 | Zone 36 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13085 | Zone 37 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13086 | Zone 38 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13087 | Zone 39 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13088 | Zone 40 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13089 | Zone 41 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13090 | Zone 42 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13091 | Zone 43 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13092 | Zone 44 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13093 | Zone 45 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13094 | Zone 46 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13095 | Zone 47 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13096 | Zone 48 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13097 | Zone 49 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13098 | Zone 50 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13099 | Zone 51 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13100 | Zone 52 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13101 | Zone 53 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13102 | Zone 54 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13103 | Zone 55 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13104 | Zone 56 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13105 | Zone 57 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13106 | Zone 58 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13107 | Zone 59 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13108 | Zone 60 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13109 | Zone 61 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13110 | Zone 62 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13111 | Zone 63 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13112 | Zone 64 | Day 3 Event 3 End Time | 0 | 1440 | min
4:13113 | Zone 1 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13114 | Zone 2 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13115 | Zone 3 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13116 | Zone 4 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13117 | Zone 5 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13118 | Zone 6 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13119 | Zone 7 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13120 | Zone 8 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13121 | Zone 9 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13122 | Zone 10 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13123 | Zone 11 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13124 | Zone 12 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13125 | Zone 13 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13126 | Zone 14 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13127 | Zone 15 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13128 | Zone 16 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13129 | Zone 17 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13130 | Zone 18 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13131 | Zone 19 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13132 | Zone 20 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13133 | Zone 21 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13134 | Zone 22 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13135 | Zone 23 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13136 | Zone 24 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13137 | Zone 25 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13138 | Zone 26 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13139 | Zone 27 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13140 | Zone 28 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13141 | Zone 29 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13142 | Zone 30 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13143 | Zone 31 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13144 | Zone 32 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13145 | Zone 33 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13146 | Zone 34 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13147 | Zone 35 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13148 | Zone 36 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13149 | Zone 37 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13150 | Zone 38 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13151 | Zone 39 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13152 | Zone 40 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13153 | Zone 41 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13154 | Zone 42 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13155 | Zone 43 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13156 | Zone 44 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13157 | Zone 45 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13158 | Zone 46 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13159 | Zone 47 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13160 | Zone 48 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13161 | Zone 49 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13162 | Zone 50 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13163 | Zone 51 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13164 | Zone 52 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13165 | Zone 53 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13166 | Zone 54 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13167 | Zone 55 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13168 | Zone 56 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13169 | Zone 57 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13170 | Zone 58 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13171 | Zone 59 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13172 | Zone 60 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13173 | Zone 61 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13174 | Zone 62 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13175 | Zone 63 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13176 | Zone 64 | Day 4 Event 1 Start Time | 0 | 1440 | min
4:13177 | Zone 1 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13178 | Zone 2 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13179 | Zone 3 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13180 | Zone 4 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13181 | Zone 5 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13182 | Zone 6 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13183 | Zone 7 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13184 | Zone 8 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13185 | Zone 9 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13186 | Zone 10 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13187 | Zone 11 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13188 | Zone 12 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13189 | Zone 13 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13190 | Zone 14 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13191 | Zone 15 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13192 | Zone 16 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13193 | Zone 17 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13194 | Zone 18 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13195 | Zone 19 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13196 | Zone 20 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13197 | Zone 21 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13198 | Zone 22 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13199 | Zone 23 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13200 | Zone 24 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13201 | Zone 25 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13202 | Zone 26 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13203 | Zone 27 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13204 | Zone 28 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13205 | Zone 29 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13206 | Zone 30 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13207 | Zone 31 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13208 | Zone 32 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13209 | Zone 33 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13210 | Zone 34 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13211 | Zone 35 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13212 | Zone 36 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13213 | Zone 37 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13214 | Zone 38 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13215 | Zone 39 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13216 | Zone 40 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13217 | Zone 41 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13218 | Zone 42 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13219 | Zone 43 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13220 | Zone 44 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13221 | Zone 45 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13222 | Zone 46 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13223 | Zone 47 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13224 | Zone 48 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13225 | Zone 49 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13226 | Zone 50 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13227 | Zone 51 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13228 | Zone 52 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13229 | Zone 53 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13230 | Zone 54 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13231 | Zone 55 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13232 | Zone 56 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13233 | Zone 57 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13234 | Zone 58 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13235 | Zone 59 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13236 | Zone 60 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13237 | Zone 61 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13238 | Zone 62 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13239 | Zone 63 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13240 | Zone 64 | Day 4 Event 1 End Time | 0 | 1440 | min
4:13241 | Zone 1 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13242 | Zone 2 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13243 | Zone 3 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13244 | Zone 4 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13245 | Zone 5 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13246 | Zone 6 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13247 | Zone 7 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13248 | Zone 8 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13249 | Zone 9 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13250 | Zone 10 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13251 | Zone 11 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13252 | Zone 12 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13253 | Zone 13 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13254 | Zone 14 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13255 | Zone 15 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13256 | Zone 16 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13257 | Zone 17 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13258 | Zone 18 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13259 | Zone 19 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13260 | Zone 20 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13261 | Zone 21 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13262 | Zone 22 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13263 | Zone 23 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13264 | Zone 24 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13265 | Zone 25 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13266 | Zone 26 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13267 | Zone 27 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13268 | Zone 28 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13269 | Zone 29 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13270 | Zone 30 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13271 | Zone 31 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13272 | Zone 32 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13273 | Zone 33 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13274 | Zone 34 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13275 | Zone 35 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13276 | Zone 36 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13277 | Zone 37 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13278 | Zone 38 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13279 | Zone 39 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13280 | Zone 40 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13281 | Zone 41 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13282 | Zone 42 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13283 | Zone 43 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13284 | Zone 44 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13285 | Zone 45 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13286 | Zone 46 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13287 | Zone 47 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13288 | Zone 48 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13289 | Zone 49 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13290 | Zone 50 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13291 | Zone 51 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13292 | Zone 52 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13293 | Zone 53 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13294 | Zone 54 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13295 | Zone 55 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13296 | Zone 56 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13297 | Zone 57 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13298 | Zone 58 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13299 | Zone 59 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13300 | Zone 60 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13301 | Zone 61 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13302 | Zone 62 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13303 | Zone 63 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13304 | Zone 64 | Day 4 Event 2 Start Time | 0 | 1440 | min
4:13305 | Zone 1 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13306 | Zone 2 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13307 | Zone 3 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13308 | Zone 4 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13309 | Zone 5 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13310 | Zone 6 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13311 | Zone 7 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13312 | Zone 8 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13313 | Zone 9 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13314 | Zone 10 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13315 | Zone 11 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13316 | Zone 12 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13317 | Zone 13 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13318 | Zone 14 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13319 | Zone 15 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13320 | Zone 16 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13321 | Zone 17 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13322 | Zone 18 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13323 | Zone 19 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13324 | Zone 20 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13325 | Zone 21 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13326 | Zone 22 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13327 | Zone 23 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13328 | Zone 24 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13329 | Zone 25 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13330 | Zone 26 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13331 | Zone 27 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13332 | Zone 28 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13333 | Zone 29 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13334 | Zone 30 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13335 | Zone 31 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13336 | Zone 32 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13337 | Zone 33 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13338 | Zone 34 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13339 | Zone 35 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13340 | Zone 36 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13341 | Zone 37 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13342 | Zone 38 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13343 | Zone 39 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13344 | Zone 40 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13345 | Zone 41 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13346 | Zone 42 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13347 | Zone 43 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13348 | Zone 44 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13349 | Zone 45 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13350 | Zone 46 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13351 | Zone 47 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13352 | Zone 48 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13353 | Zone 49 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13354 | Zone 50 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13355 | Zone 51 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13356 | Zone 52 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13357 | Zone 53 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13358 | Zone 54 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13359 | Zone 55 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13360 | Zone 56 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13361 | Zone 57 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13362 | Zone 58 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13363 | Zone 59 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13364 | Zone 60 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13365 | Zone 61 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13366 | Zone 62 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13367 | Zone 63 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13368 | Zone 64 | Day 4 Event 2 End Time | 0 | 1440 | min
4:13369 | Zone 1 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13370 | Zone 2 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13371 | Zone 3 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13372 | Zone 4 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13373 | Zone 5 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13374 | Zone 6 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13375 | Zone 7 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13376 | Zone 8 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13377 | Zone 9 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13378 | Zone 10 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13379 | Zone 11 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13380 | Zone 12 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13381 | Zone 13 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13382 | Zone 14 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13383 | Zone 15 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13384 | Zone 16 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13385 | Zone 17 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13386 | Zone 18 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13387 | Zone 19 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13388 | Zone 20 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13389 | Zone 21 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13390 | Zone 22 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13391 | Zone 23 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13392 | Zone 24 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13393 | Zone 25 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13394 | Zone 26 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13395 | Zone 27 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13396 | Zone 28 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13397 | Zone 29 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13398 | Zone 30 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13399 | Zone 31 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13400 | Zone 32 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13401 | Zone 33 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13402 | Zone 34 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13403 | Zone 35 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13404 | Zone 36 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13405 | Zone 37 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13406 | Zone 38 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13407 | Zone 39 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13408 | Zone 40 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13409 | Zone 41 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13410 | Zone 42 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13411 | Zone 43 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13412 | Zone 44 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13413 | Zone 45 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13414 | Zone 46 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13415 | Zone 47 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13416 | Zone 48 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13417 | Zone 49 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13418 | Zone 50 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13419 | Zone 51 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13420 | Zone 52 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13421 | Zone 53 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13422 | Zone 54 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13423 | Zone 55 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13424 | Zone 56 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13425 | Zone 57 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13426 | Zone 58 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13427 | Zone 59 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13428 | Zone 60 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13429 | Zone 61 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13430 | Zone 62 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13431 | Zone 63 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13432 | Zone 64 | Day 4 Event 3 Start Time | 0 | 1440 | min
4:13433 | Zone 1 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13434 | Zone 2 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13435 | Zone 3 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13436 | Zone 4 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13437 | Zone 5 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13438 | Zone 6 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13439 | Zone 7 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13440 | Zone 8 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13441 | Zone 9 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13442 | Zone 10 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13443 | Zone 11 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13444 | Zone 12 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13445 | Zone 13 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13446 | Zone 14 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13447 | Zone 15 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13448 | Zone 16 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13449 | Zone 17 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13450 | Zone 18 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13451 | Zone 19 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13452 | Zone 20 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13453 | Zone 21 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13454 | Zone 22 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13455 | Zone 23 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13456 | Zone 24 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13457 | Zone 25 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13458 | Zone 26 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13459 | Zone 27 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13460 | Zone 28 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13461 | Zone 29 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13462 | Zone 30 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13463 | Zone 31 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13464 | Zone 32 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13465 | Zone 33 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13466 | Zone 34 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13467 | Zone 35 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13468 | Zone 36 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13469 | Zone 37 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13470 | Zone 38 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13471 | Zone 39 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13472 | Zone 40 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13473 | Zone 41 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13474 | Zone 42 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13475 | Zone 43 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13476 | Zone 44 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13477 | Zone 45 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13478 | Zone 46 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13479 | Zone 47 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13480 | Zone 48 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13481 | Zone 49 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13482 | Zone 50 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13483 | Zone 51 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13484 | Zone 52 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13485 | Zone 53 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13486 | Zone 54 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13487 | Zone 55 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13488 | Zone 56 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13489 | Zone 57 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13490 | Zone 58 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13491 | Zone 59 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13492 | Zone 60 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13493 | Zone 61 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13494 | Zone 62 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13495 | Zone 63 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13496 | Zone 64 | Day 4 Event 3 End Time | 0 | 1440 | min
4:13497 | Zone 1 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13498 | Zone 2 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13499 | Zone 3 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13500 | Zone 4 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13501 | Zone 5 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13502 | Zone 6 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13503 | Zone 7 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13504 | Zone 8 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13505 | Zone 9 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13506 | Zone 10 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13507 | Zone 11 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13508 | Zone 12 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13509 | Zone 13 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13510 | Zone 14 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13511 | Zone 15 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13512 | Zone 16 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13513 | Zone 17 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13514 | Zone 18 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13515 | Zone 19 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13516 | Zone 20 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13517 | Zone 21 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13518 | Zone 22 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13519 | Zone 23 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13520 | Zone 24 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13521 | Zone 25 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13522 | Zone 26 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13523 | Zone 27 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13524 | Zone 28 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13525 | Zone 29 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13526 | Zone 30 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13527 | Zone 31 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13528 | Zone 32 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13529 | Zone 33 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13530 | Zone 34 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13531 | Zone 35 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13532 | Zone 36 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13533 | Zone 37 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13534 | Zone 38 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13535 | Zone 39 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13536 | Zone 40 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13537 | Zone 41 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13538 | Zone 42 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13539 | Zone 43 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13540 | Zone 44 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13541 | Zone 45 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13542 | Zone 46 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13543 | Zone 47 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13544 | Zone 48 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13545 | Zone 49 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13546 | Zone 50 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13547 | Zone 51 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13548 | Zone 52 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13549 | Zone 53 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13550 | Zone 54 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13551 | Zone 55 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13552 | Zone 56 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13553 | Zone 57 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13554 | Zone 58 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13555 | Zone 59 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13556 | Zone 60 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13557 | Zone 61 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13558 | Zone 62 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13559 | Zone 63 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13560 | Zone 64 | Day 5 Event 1 Start Time | 0 | 1440 | min
4:13561 | Zone 1 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13562 | Zone 2 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13563 | Zone 3 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13564 | Zone 4 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13565 | Zone 5 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13566 | Zone 6 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13567 | Zone 7 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13568 | Zone 8 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13569 | Zone 9 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13570 | Zone 10 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13571 | Zone 11 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13572 | Zone 12 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13573 | Zone 13 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13574 | Zone 14 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13575 | Zone 15 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13576 | Zone 16 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13577 | Zone 17 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13578 | Zone 18 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13579 | Zone 19 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13580 | Zone 20 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13581 | Zone 21 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13582 | Zone 22 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13583 | Zone 23 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13584 | Zone 24 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13585 | Zone 25 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13586 | Zone 26 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13587 | Zone 27 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13588 | Zone 28 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13589 | Zone 29 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13590 | Zone 30 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13591 | Zone 31 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13592 | Zone 32 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13593 | Zone 33 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13594 | Zone 34 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13595 | Zone 35 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13596 | Zone 36 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13597 | Zone 37 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13598 | Zone 38 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13599 | Zone 39 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13600 | Zone 40 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13601 | Zone 41 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13602 | Zone 42 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13603 | Zone 43 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13604 | Zone 44 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13605 | Zone 45 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13606 | Zone 46 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13607 | Zone 47 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13608 | Zone 48 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13609 | Zone 49 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13610 | Zone 50 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13611 | Zone 51 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13612 | Zone 52 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13613 | Zone 53 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13614 | Zone 54 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13615 | Zone 55 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13616 | Zone 56 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13617 | Zone 57 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13618 | Zone 58 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13619 | Zone 59 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13620 | Zone 60 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13621 | Zone 61 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13622 | Zone 62 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13623 | Zone 63 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13624 | Zone 64 | Day 5 Event 1 End Time | 0 | 1440 | min
4:13625 | Zone 1 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13626 | Zone 2 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13627 | Zone 3 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13628 | Zone 4 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13629 | Zone 5 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13630 | Zone 6 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13631 | Zone 7 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13632 | Zone 8 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13633 | Zone 9 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13634 | Zone 10 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13635 | Zone 11 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13636 | Zone 12 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13637 | Zone 13 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13638 | Zone 14 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13639 | Zone 15 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13640 | Zone 16 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13641 | Zone 17 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13642 | Zone 18 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13643 | Zone 19 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13644 | Zone 20 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13645 | Zone 21 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13646 | Zone 22 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13647 | Zone 23 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13648 | Zone 24 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13649 | Zone 25 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13650 | Zone 26 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13651 | Zone 27 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13652 | Zone 28 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13653 | Zone 29 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13654 | Zone 30 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13655 | Zone 31 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13656 | Zone 32 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13657 | Zone 33 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13658 | Zone 34 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13659 | Zone 35 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13660 | Zone 36 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13661 | Zone 37 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13662 | Zone 38 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13663 | Zone 39 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13664 | Zone 40 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13665 | Zone 41 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13666 | Zone 42 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13667 | Zone 43 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13668 | Zone 44 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13669 | Zone 45 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13670 | Zone 46 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13671 | Zone 47 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13672 | Zone 48 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13673 | Zone 49 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13674 | Zone 50 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13675 | Zone 51 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13676 | Zone 52 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13677 | Zone 53 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13678 | Zone 54 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13679 | Zone 55 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13680 | Zone 56 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13681 | Zone 57 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13682 | Zone 58 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13683 | Zone 59 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13684 | Zone 60 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13685 | Zone 61 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13686 | Zone 62 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13687 | Zone 63 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13688 | Zone 64 | Day 5 Event 2 Start Time | 0 | 1440 | min
4:13689 | Zone 1 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13690 | Zone 2 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13691 | Zone 3 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13692 | Zone 4 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13693 | Zone 5 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13694 | Zone 6 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13695 | Zone 7 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13696 | Zone 8 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13697 | Zone 9 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13698 | Zone 10 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13699 | Zone 11 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13700 | Zone 12 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13701 | Zone 13 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13702 | Zone 14 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13703 | Zone 15 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13704 | Zone 16 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13705 | Zone 17 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13706 | Zone 18 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13707 | Zone 19 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13708 | Zone 20 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13709 | Zone 21 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13710 | Zone 22 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13711 | Zone 23 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13712 | Zone 24 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13713 | Zone 25 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13714 | Zone 26 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13715 | Zone 27 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13716 | Zone 28 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13717 | Zone 29 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13718 | Zone 30 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13719 | Zone 31 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13720 | Zone 32 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13721 | Zone 33 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13722 | Zone 34 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13723 | Zone 35 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13724 | Zone 36 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13725 | Zone 37 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13726 | Zone 38 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13727 | Zone 39 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13728 | Zone 40 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13729 | Zone 41 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13730 | Zone 42 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13731 | Zone 43 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13732 | Zone 44 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13733 | Zone 45 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13734 | Zone 46 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13735 | Zone 47 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13736 | Zone 48 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13737 | Zone 49 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13738 | Zone 50 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13739 | Zone 51 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13740 | Zone 52 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13741 | Zone 53 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13742 | Zone 54 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13743 | Zone 55 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13744 | Zone 56 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13745 | Zone 57 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13746 | Zone 58 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13747 | Zone 59 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13748 | Zone 60 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13749 | Zone 61 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13750 | Zone 62 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13751 | Zone 63 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13752 | Zone 64 | Day 5 Event 2 End Time | 0 | 1440 | min
4:13753 | Zone 1 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13754 | Zone 2 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13755 | Zone 3 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13756 | Zone 4 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13757 | Zone 5 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13758 | Zone 6 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13759 | Zone 7 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13760 | Zone 8 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13761 | Zone 9 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13762 | Zone 10 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13763 | Zone 11 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13764 | Zone 12 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13765 | Zone 13 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13766 | Zone 14 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13767 | Zone 15 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13768 | Zone 16 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13769 | Zone 17 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13770 | Zone 18 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13771 | Zone 19 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13772 | Zone 20 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13773 | Zone 21 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13774 | Zone 22 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13775 | Zone 23 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13776 | Zone 24 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13777 | Zone 25 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13778 | Zone 26 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13779 | Zone 27 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13780 | Zone 28 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13781 | Zone 29 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13782 | Zone 30 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13783 | Zone 31 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13784 | Zone 32 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13785 | Zone 33 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13786 | Zone 34 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13787 | Zone 35 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13788 | Zone 36 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13789 | Zone 37 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13790 | Zone 38 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13791 | Zone 39 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13792 | Zone 40 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13793 | Zone 41 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13794 | Zone 42 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13795 | Zone 43 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13796 | Zone 44 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13797 | Zone 45 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13798 | Zone 46 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13799 | Zone 47 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13800 | Zone 48 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13801 | Zone 49 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13802 | Zone 50 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13803 | Zone 51 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13804 | Zone 52 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13805 | Zone 53 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13806 | Zone 54 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13807 | Zone 55 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13808 | Zone 56 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13809 | Zone 57 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13810 | Zone 58 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13811 | Zone 59 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13812 | Zone 60 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13813 | Zone 61 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13814 | Zone 62 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13815 | Zone 63 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13816 | Zone 64 | Day 5 Event 3 Start Time | 0 | 1440 | min
4:13817 | Zone 1 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13818 | Zone 2 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13819 | Zone 3 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13820 | Zone 4 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13821 | Zone 5 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13822 | Zone 6 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13823 | Zone 7 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13824 | Zone 8 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13825 | Zone 9 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13826 | Zone 10 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13827 | Zone 11 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13828 | Zone 12 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13829 | Zone 13 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13830 | Zone 14 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13831 | Zone 15 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13832 | Zone 16 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13833 | Zone 17 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13834 | Zone 18 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13835 | Zone 19 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13836 | Zone 20 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13837 | Zone 21 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13838 | Zone 22 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13839 | Zone 23 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13840 | Zone 24 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13841 | Zone 25 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13842 | Zone 26 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13843 | Zone 27 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13844 | Zone 28 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13845 | Zone 29 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13846 | Zone 30 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13847 | Zone 31 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13848 | Zone 32 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13849 | Zone 33 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13850 | Zone 34 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13851 | Zone 35 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13852 | Zone 36 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13853 | Zone 37 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13854 | Zone 38 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13855 | Zone 39 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13856 | Zone 40 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13857 | Zone 41 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13858 | Zone 42 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13859 | Zone 43 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13860 | Zone 44 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13861 | Zone 45 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13862 | Zone 46 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13863 | Zone 47 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13864 | Zone 48 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13865 | Zone 49 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13866 | Zone 50 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13867 | Zone 51 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13868 | Zone 52 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13869 | Zone 53 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13870 | Zone 54 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13871 | Zone 55 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13872 | Zone 56 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13873 | Zone 57 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13874 | Zone 58 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13875 | Zone 59 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13876 | Zone 60 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13877 | Zone 61 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13878 | Zone 62 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13879 | Zone 63 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13880 | Zone 64 | Day 5 Event 3 End Time | 0 | 1440 | min
4:13881 | Zone 1 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13882 | Zone 2 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13883 | Zone 3 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13884 | Zone 4 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13885 | Zone 5 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13886 | Zone 6 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13887 | Zone 7 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13888 | Zone 8 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13889 | Zone 9 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13890 | Zone 10 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13891 | Zone 11 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13892 | Zone 12 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13893 | Zone 13 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13894 | Zone 14 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13895 | Zone 15 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13896 | Zone 16 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13897 | Zone 17 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13898 | Zone 18 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13899 | Zone 19 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13900 | Zone 20 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13901 | Zone 21 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13902 | Zone 22 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13903 | Zone 23 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13904 | Zone 24 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13905 | Zone 25 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13906 | Zone 26 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13907 | Zone 27 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13908 | Zone 28 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13909 | Zone 29 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13910 | Zone 30 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13911 | Zone 31 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13912 | Zone 32 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13913 | Zone 33 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13914 | Zone 34 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13915 | Zone 35 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13916 | Zone 36 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13917 | Zone 37 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13918 | Zone 38 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13919 | Zone 39 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13920 | Zone 40 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13921 | Zone 41 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13922 | Zone 42 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13923 | Zone 43 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13924 | Zone 44 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13925 | Zone 45 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13926 | Zone 46 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13927 | Zone 47 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13928 | Zone 48 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13929 | Zone 49 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13930 | Zone 50 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13931 | Zone 51 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13932 | Zone 52 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13933 | Zone 53 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13934 | Zone 54 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13935 | Zone 55 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13936 | Zone 56 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13937 | Zone 57 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13938 | Zone 58 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13939 | Zone 59 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13940 | Zone 60 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13941 | Zone 61 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13942 | Zone 62 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13943 | Zone 63 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13944 | Zone 64 | Day 6 Event 1 Start Time | 0 | 1440 | min
4:13945 | Zone 1 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13946 | Zone 2 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13947 | Zone 3 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13948 | Zone 4 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13949 | Zone 5 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13950 | Zone 6 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13951 | Zone 7 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13952 | Zone 8 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13953 | Zone 9 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13954 | Zone 10 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13955 | Zone 11 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13956 | Zone 12 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13957 | Zone 13 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13958 | Zone 14 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13959 | Zone 15 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13960 | Zone 16 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13961 | Zone 17 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13962 | Zone 18 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13963 | Zone 19 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13964 | Zone 20 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13965 | Zone 21 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13966 | Zone 22 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13967 | Zone 23 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13968 | Zone 24 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13969 | Zone 25 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13970 | Zone 26 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13971 | Zone 27 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13972 | Zone 28 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13973 | Zone 29 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13974 | Zone 30 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13975 | Zone 31 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13976 | Zone 32 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13977 | Zone 33 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13978 | Zone 34 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13979 | Zone 35 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13980 | Zone 36 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13981 | Zone 37 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13982 | Zone 38 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13983 | Zone 39 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13984 | Zone 40 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13985 | Zone 41 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13986 | Zone 42 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13987 | Zone 43 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13988 | Zone 44 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13989 | Zone 45 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13990 | Zone 46 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13991 | Zone 47 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13992 | Zone 48 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13993 | Zone 49 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13994 | Zone 50 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13995 | Zone 51 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13996 | Zone 52 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13997 | Zone 53 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13998 | Zone 54 | Day 6 Event 1 End Time | 0 | 1440 | min
4:13999 | Zone 55 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14000 | Zone 56 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14001 | Zone 57 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14002 | Zone 58 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14003 | Zone 59 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14004 | Zone 60 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14005 | Zone 61 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14006 | Zone 62 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14007 | Zone 63 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14008 | Zone 64 | Day 6 Event 1 End Time | 0 | 1440 | min
4:14009 | Zone 1 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14010 | Zone 2 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14011 | Zone 3 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14012 | Zone 4 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14013 | Zone 5 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14014 | Zone 6 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14015 | Zone 7 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14016 | Zone 8 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14017 | Zone 9 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14018 | Zone 10 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14019 | Zone 11 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14020 | Zone 12 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14021 | Zone 13 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14022 | Zone 14 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14023 | Zone 15 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14024 | Zone 16 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14025 | Zone 17 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14026 | Zone 18 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14027 | Zone 19 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14028 | Zone 20 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14029 | Zone 21 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14030 | Zone 22 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14031 | Zone 23 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14032 | Zone 24 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14033 | Zone 25 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14034 | Zone 26 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14035 | Zone 27 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14036 | Zone 28 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14037 | Zone 29 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14038 | Zone 30 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14039 | Zone 31 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14040 | Zone 32 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14041 | Zone 33 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14042 | Zone 34 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14043 | Zone 35 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14044 | Zone 36 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14045 | Zone 37 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14046 | Zone 38 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14047 | Zone 39 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14048 | Zone 40 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14049 | Zone 41 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14050 | Zone 42 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14051 | Zone 43 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14052 | Zone 44 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14053 | Zone 45 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14054 | Zone 46 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14055 | Zone 47 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14056 | Zone 48 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14057 | Zone 49 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14058 | Zone 50 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14059 | Zone 51 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14060 | Zone 52 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14061 | Zone 53 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14062 | Zone 54 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14063 | Zone 55 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14064 | Zone 56 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14065 | Zone 57 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14066 | Zone 58 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14067 | Zone 59 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14068 | Zone 60 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14069 | Zone 61 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14070 | Zone 62 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14071 | Zone 63 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14072 | Zone 64 | Day 6 Event 2 Start Time | 0 | 1440 | min
4:14073 | Zone 1 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14074 | Zone 2 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14075 | Zone 3 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14076 | Zone 4 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14077 | Zone 5 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14078 | Zone 6 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14079 | Zone 7 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14080 | Zone 8 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14081 | Zone 9 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14082 | Zone 10 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14083 | Zone 11 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14084 | Zone 12 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14085 | Zone 13 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14086 | Zone 14 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14087 | Zone 15 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14088 | Zone 16 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14089 | Zone 17 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14090 | Zone 18 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14091 | Zone 19 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14092 | Zone 20 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14093 | Zone 21 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14094 | Zone 22 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14095 | Zone 23 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14096 | Zone 24 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14097 | Zone 25 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14098 | Zone 26 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14099 | Zone 27 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14100 | Zone 28 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14101 | Zone 29 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14102 | Zone 30 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14103 | Zone 31 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14104 | Zone 32 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14105 | Zone 33 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14106 | Zone 34 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14107 | Zone 35 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14108 | Zone 36 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14109 | Zone 37 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14110 | Zone 38 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14111 | Zone 39 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14112 | Zone 40 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14113 | Zone 41 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14114 | Zone 42 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14115 | Zone 43 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14116 | Zone 44 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14117 | Zone 45 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14118 | Zone 46 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14119 | Zone 47 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14120 | Zone 48 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14121 | Zone 49 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14122 | Zone 50 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14123 | Zone 51 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14124 | Zone 52 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14125 | Zone 53 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14126 | Zone 54 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14127 | Zone 55 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14128 | Zone 56 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14129 | Zone 57 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14130 | Zone 58 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14131 | Zone 59 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14132 | Zone 60 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14133 | Zone 61 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14134 | Zone 62 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14135 | Zone 63 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14136 | Zone 64 | Day 6 Event 2 End Time | 0 | 1440 | min
4:14137 | Zone 1 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14138 | Zone 2 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14139 | Zone 3 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14140 | Zone 4 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14141 | Zone 5 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14142 | Zone 6 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14143 | Zone 7 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14144 | Zone 8 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14145 | Zone 9 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14146 | Zone 10 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14147 | Zone 11 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14148 | Zone 12 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14149 | Zone 13 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14150 | Zone 14 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14151 | Zone 15 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14152 | Zone 16 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14153 | Zone 17 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14154 | Zone 18 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14155 | Zone 19 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14156 | Zone 20 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14157 | Zone 21 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14158 | Zone 22 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14159 | Zone 23 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14160 | Zone 24 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14161 | Zone 25 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14162 | Zone 26 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14163 | Zone 27 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14164 | Zone 28 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14165 | Zone 29 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14166 | Zone 30 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14167 | Zone 31 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14168 | Zone 32 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14169 | Zone 33 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14170 | Zone 34 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14171 | Zone 35 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14172 | Zone 36 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14173 | Zone 37 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14174 | Zone 38 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14175 | Zone 39 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14176 | Zone 40 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14177 | Zone 41 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14178 | Zone 42 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14179 | Zone 43 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14180 | Zone 44 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14181 | Zone 45 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14182 | Zone 46 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14183 | Zone 47 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14184 | Zone 48 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14185 | Zone 49 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14186 | Zone 50 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14187 | Zone 51 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14188 | Zone 52 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14189 | Zone 53 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14190 | Zone 54 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14191 | Zone 55 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14192 | Zone 56 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14193 | Zone 57 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14194 | Zone 58 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14195 | Zone 59 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14196 | Zone 60 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14197 | Zone 61 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14198 | Zone 62 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14199 | Zone 63 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14200 | Zone 64 | Day 6 Event 3 Start Time | 0 | 1440 | min
4:14201 | Zone 1 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14202 | Zone 2 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14203 | Zone 3 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14204 | Zone 4 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14205 | Zone 5 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14206 | Zone 6 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14207 | Zone 7 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14208 | Zone 8 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14209 | Zone 9 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14210 | Zone 10 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14211 | Zone 11 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14212 | Zone 12 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14213 | Zone 13 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14214 | Zone 14 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14215 | Zone 15 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14216 | Zone 16 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14217 | Zone 17 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14218 | Zone 18 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14219 | Zone 19 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14220 | Zone 20 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14221 | Zone 21 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14222 | Zone 22 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14223 | Zone 23 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14224 | Zone 24 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14225 | Zone 25 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14226 | Zone 26 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14227 | Zone 27 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14228 | Zone 28 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14229 | Zone 29 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14230 | Zone 30 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14231 | Zone 31 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14232 | Zone 32 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14233 | Zone 33 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14234 | Zone 34 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14235 | Zone 35 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14236 | Zone 36 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14237 | Zone 37 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14238 | Zone 38 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14239 | Zone 39 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14240 | Zone 40 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14241 | Zone 41 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14242 | Zone 42 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14243 | Zone 43 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14244 | Zone 44 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14245 | Zone 45 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14246 | Zone 46 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14247 | Zone 47 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14248 | Zone 48 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14249 | Zone 49 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14250 | Zone 50 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14251 | Zone 51 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14252 | Zone 52 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14253 | Zone 53 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14254 | Zone 54 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14255 | Zone 55 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14256 | Zone 56 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14257 | Zone 57 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14258 | Zone 58 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14259 | Zone 59 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14260 | Zone 60 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14261 | Zone 61 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14262 | Zone 62 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14263 | Zone 63 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14264 | Zone 64 | Day 6 Event 3 End Time | 0 | 1440 | min
4:14265 | Zone 1 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14266 | Zone 2 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14267 | Zone 3 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14268 | Zone 4 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14269 | Zone 5 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14270 | Zone 6 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14271 | Zone 7 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14272 | Zone 8 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14273 | Zone 9 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14274 | Zone 10 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14275 | Zone 11 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14276 | Zone 12 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14277 | Zone 13 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14278 | Zone 14 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14279 | Zone 15 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14280 | Zone 16 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14281 | Zone 17 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14282 | Zone 18 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14283 | Zone 19 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14284 | Zone 20 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14285 | Zone 21 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14286 | Zone 22 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14287 | Zone 23 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14288 | Zone 24 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14289 | Zone 25 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14290 | Zone 26 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14291 | Zone 27 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14292 | Zone 28 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14293 | Zone 29 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14294 | Zone 30 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14295 | Zone 31 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14296 | Zone 32 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14297 | Zone 33 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14298 | Zone 34 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14299 | Zone 35 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14300 | Zone 36 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14301 | Zone 37 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14302 | Zone 38 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14303 | Zone 39 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14304 | Zone 40 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14305 | Zone 41 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14306 | Zone 42 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14307 | Zone 43 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14308 | Zone 44 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14309 | Zone 45 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14310 | Zone 46 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14311 | Zone 47 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14312 | Zone 48 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14313 | Zone 49 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14314 | Zone 50 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14315 | Zone 51 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14316 | Zone 52 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14317 | Zone 53 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14318 | Zone 54 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14319 | Zone 55 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14320 | Zone 56 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14321 | Zone 57 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14322 | Zone 58 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14323 | Zone 59 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14324 | Zone 60 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14325 | Zone 61 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14326 | Zone 62 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14327 | Zone 63 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14328 | Zone 64 | Day 7 Event 1 Start Time | 0 | 1440 | min
4:14329 | Zone 1 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14330 | Zone 2 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14331 | Zone 3 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14332 | Zone 4 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14333 | Zone 5 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14334 | Zone 6 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14335 | Zone 7 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14336 | Zone 8 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14337 | Zone 9 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14338 | Zone 10 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14339 | Zone 11 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14340 | Zone 12 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14341 | Zone 13 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14342 | Zone 14 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14343 | Zone 15 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14344 | Zone 16 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14345 | Zone 17 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14346 | Zone 18 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14347 | Zone 19 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14348 | Zone 20 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14349 | Zone 21 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14350 | Zone 22 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14351 | Zone 23 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14352 | Zone 24 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14353 | Zone 25 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14354 | Zone 26 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14355 | Zone 27 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14356 | Zone 28 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14357 | Zone 29 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14358 | Zone 30 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14359 | Zone 31 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14360 | Zone 32 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14361 | Zone 33 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14362 | Zone 34 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14363 | Zone 35 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14364 | Zone 36 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14365 | Zone 37 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14366 | Zone 38 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14367 | Zone 39 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14368 | Zone 40 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14369 | Zone 41 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14370 | Zone 42 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14371 | Zone 43 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14372 | Zone 44 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14373 | Zone 45 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14374 | Zone 46 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14375 | Zone 47 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14376 | Zone 48 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14377 | Zone 49 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14378 | Zone 50 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14379 | Zone 51 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14380 | Zone 52 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14381 | Zone 53 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14382 | Zone 54 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14383 | Zone 55 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14384 | Zone 56 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14385 | Zone 57 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14386 | Zone 58 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14387 | Zone 59 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14388 | Zone 60 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14389 | Zone 61 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14390 | Zone 62 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14391 | Zone 63 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14392 | Zone 64 | Day 7 Event 1 End Time | 0 | 1440 | min
4:14393 | Zone 1 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14394 | Zone 2 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14395 | Zone 3 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14396 | Zone 4 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14397 | Zone 5 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14398 | Zone 6 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14399 | Zone 7 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14400 | Zone 8 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14401 | Zone 9 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14402 | Zone 10 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14403 | Zone 11 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14404 | Zone 12 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14405 | Zone 13 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14406 | Zone 14 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14407 | Zone 15 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14408 | Zone 16 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14409 | Zone 17 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14410 | Zone 18 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14411 | Zone 19 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14412 | Zone 20 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14413 | Zone 21 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14414 | Zone 22 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14415 | Zone 23 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14416 | Zone 24 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14417 | Zone 25 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14418 | Zone 26 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14419 | Zone 27 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14420 | Zone 28 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14421 | Zone 29 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14422 | Zone 30 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14423 | Zone 31 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14424 | Zone 32 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14425 | Zone 33 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14426 | Zone 34 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14427 | Zone 35 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14428 | Zone 36 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14429 | Zone 37 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14430 | Zone 38 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14431 | Zone 39 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14432 | Zone 40 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14433 | Zone 41 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14434 | Zone 42 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14435 | Zone 43 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14436 | Zone 44 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14437 | Zone 45 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14438 | Zone 46 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14439 | Zone 47 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14440 | Zone 48 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14441 | Zone 49 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14442 | Zone 50 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14443 | Zone 51 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14444 | Zone 52 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14445 | Zone 53 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14446 | Zone 54 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14447 | Zone 55 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14448 | Zone 56 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14449 | Zone 57 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14450 | Zone 58 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14451 | Zone 59 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14452 | Zone 60 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14453 | Zone 61 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14454 | Zone 62 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14455 | Zone 63 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14456 | Zone 64 | Day 7 Event 2 Start Time | 0 | 1440 | min
4:14457 | Zone 1 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14458 | Zone 2 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14459 | Zone 3 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14460 | Zone 4 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14461 | Zone 5 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14462 | Zone 6 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14463 | Zone 7 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14464 | Zone 8 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14465 | Zone 9 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14466 | Zone 10 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14467 | Zone 11 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14468 | Zone 12 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14469 | Zone 13 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14470 | Zone 14 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14471 | Zone 15 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14472 | Zone 16 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14473 | Zone 17 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14474 | Zone 18 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14475 | Zone 19 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14476 | Zone 20 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14477 | Zone 21 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14478 | Zone 22 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14479 | Zone 23 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14480 | Zone 24 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14481 | Zone 25 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14482 | Zone 26 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14483 | Zone 27 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14484 | Zone 28 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14485 | Zone 29 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14486 | Zone 30 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14487 | Zone 31 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14488 | Zone 32 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14489 | Zone 33 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14490 | Zone 34 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14491 | Zone 35 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14492 | Zone 36 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14493 | Zone 37 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14494 | Zone 38 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14495 | Zone 39 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14496 | Zone 40 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14497 | Zone 41 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14498 | Zone 42 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14499 | Zone 43 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14500 | Zone 44 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14501 | Zone 45 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14502 | Zone 46 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14503 | Zone 47 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14504 | Zone 48 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14505 | Zone 49 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14506 | Zone 50 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14507 | Zone 51 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14508 | Zone 52 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14509 | Zone 53 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14510 | Zone 54 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14511 | Zone 55 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14512 | Zone 56 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14513 | Zone 57 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14514 | Zone 58 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14515 | Zone 59 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14516 | Zone 60 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14517 | Zone 61 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14518 | Zone 62 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14519 | Zone 63 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14520 | Zone 64 | Day 7 Event 2 End Time | 0 | 1440 | min
4:14521 | Zone 1 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14522 | Zone 2 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14523 | Zone 3 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14524 | Zone 4 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14525 | Zone 5 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14526 | Zone 6 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14527 | Zone 7 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14528 | Zone 8 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14529 | Zone 9 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14530 | Zone 10 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14531 | Zone 11 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14532 | Zone 12 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14533 | Zone 13 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14534 | Zone 14 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14535 | Zone 15 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14536 | Zone 16 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14537 | Zone 17 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14538 | Zone 18 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14539 | Zone 19 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14540 | Zone 20 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14541 | Zone 21 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14542 | Zone 22 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14543 | Zone 23 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14544 | Zone 24 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14545 | Zone 25 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14546 | Zone 26 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14547 | Zone 27 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14548 | Zone 28 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14549 | Zone 29 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14550 | Zone 30 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14551 | Zone 31 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14552 | Zone 32 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14553 | Zone 33 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14554 | Zone 34 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14555 | Zone 35 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14556 | Zone 36 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14557 | Zone 37 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14558 | Zone 38 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14559 | Zone 39 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14560 | Zone 40 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14561 | Zone 41 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14562 | Zone 42 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14563 | Zone 43 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14564 | Zone 44 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14565 | Zone 45 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14566 | Zone 46 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14567 | Zone 47 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14568 | Zone 48 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14569 | Zone 49 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14570 | Zone 50 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14571 | Zone 51 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14572 | Zone 52 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14573 | Zone 53 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14574 | Zone 54 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14575 | Zone 55 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14576 | Zone 56 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14577 | Zone 57 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14578 | Zone 58 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14579 | Zone 59 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14580 | Zone 60 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14581 | Zone 61 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14582 | Zone 62 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14583 | Zone 63 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14584 | Zone 64 | Day 7 Event 3 Start Time | 0 | 1440 | min
4:14585 | Zone 1 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14586 | Zone 2 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14587 | Zone 3 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14588 | Zone 4 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14589 | Zone 5 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14590 | Zone 6 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14591 | Zone 7 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14592 | Zone 8 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14593 | Zone 9 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14594 | Zone 10 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14595 | Zone 11 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14596 | Zone 12 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14597 | Zone 13 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14598 | Zone 14 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14599 | Zone 15 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14600 | Zone 16 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14601 | Zone 17 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14602 | Zone 18 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14603 | Zone 19 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14604 | Zone 20 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14605 | Zone 21 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14606 | Zone 22 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14607 | Zone 23 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14608 | Zone 24 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14609 | Zone 25 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14610 | Zone 26 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14611 | Zone 27 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14612 | Zone 28 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14613 | Zone 29 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14614 | Zone 30 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14615 | Zone 31 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14616 | Zone 32 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14617 | Zone 33 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14618 | Zone 34 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14619 | Zone 35 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14620 | Zone 36 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14621 | Zone 37 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14622 | Zone 38 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14623 | Zone 39 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14624 | Zone 40 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14625 | Zone 41 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14626 | Zone 42 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14627 | Zone 43 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14628 | Zone 44 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14629 | Zone 45 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14630 | Zone 46 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14631 | Zone 47 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14632 | Zone 48 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14633 | Zone 49 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14634 | Zone 50 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14635 | Zone 51 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14636 | Zone 52 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14637 | Zone 53 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14638 | Zone 54 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14639 | Zone 55 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14640 | Zone 56 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14641 | Zone 57 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14642 | Zone 58 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14643 | Zone 59 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14644 | Zone 60 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14645 | Zone 61 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14646 | Zone 62 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14647 | Zone 63 | Day 7 Event 3 End Time | 0 | 1440 | min
4:14648 | Zone 64 | Day 7 Event 3 End Time | 0 | 1440 | min